## Civil works.
جدول كميات لمشروع تأهيل محطة مياه مينزا - محلية ود الماحي. Estimation & Bill Of Quantity for Menza Water Yard Wd-elmahi Locality
Item No. | Description of work | Unit | Quantity |  | Unit cost | Total cost |  | Remark
|  |  | Contract | Executed | USD | Contract | Executed
1 | Site Preparations أعمال تجهيز الموقع
1.1 | prepare the site and clean it from rubbish, Debris or any unwanted items. | service | 1 | 330 |  |  | 0
تنظيف الموقع من الأوساخ و الأنقاض أو أي مواد غير مرغوب فيها و إزالتها بعيدا من الموقع
1.2 | Transportation of all work personnel, equipments and material to the site. | L.S | 1 | 2 |  |  | 0
ترحيل المواد و الآليات و المعدات و فريق العمل الى الموقع
Sub Total1 | [6 empty] | 0
2 | Rehabilitation of water collection point إعادة تأهيل نقاط توزيع المياه
2.1 | Supply and install material for rehabilitation collection Water points as Annex2 (Distribution Points) | L.S | 1 | 2 |  |  | 0
توريد مواد لإعادة تأهيل نقاط مياه بكافة ملحقاتها بحسب الملحق 2
Sub Total 2 (1 Water Collection Point) | [6 empty] | 0
4 | Pipeline work اعمال شبكة المياه
4.1 | Excavation for pipeline trench in rocky ground depth 90cm and width of 40 cm total distance 50m from Elevated Water Tank to tap stand. All works to be done according to the specifications and instructions of the supervisor. | Ml | 600 | 330 |  |  | 0
أعمال الحفر والردم في أرض جبلية لخط الأنابيب من الخزان العلوي نقطة توزيع الحنفيات بعمق 90 سم مع تسوية الحفر بطبقة من التربة الناعمة أسفل الأنبوب ، والردم باستخدام تربة صالحة مع الرش والدك بعد الردم ، وفقا للمواصفات ، والتعليمات الموضحة ، وتعليمات المهندس المشرف
4.2 | Excavation works for pipeline trench in rocky ground depth 90cm and width 40cm,total length 600 meters from Elevated Water Tank to Health Facility. Works to be done according to the specifications and instructions of the supervisor. | Ml | 600 | 330 |  |  | 0
أعمال الحفر والردم لخط الأنابيب من الخزان العلوي الى المركز الصحي بعمق 50 سم مع تسوية الحفر بطبقة من التربة الناعمة أسفل الأنبوب ، والردم باستخدام تربة صالحة مع الرش والدك بعد الردم ، وفقا للمواصفات ، والتعليمات الموضحة ، وتعليمات المهندس المشرف
4.3 | Provide and lay Polyethylene Pipes 2" 10 bar in pipeline trench from the from Elevated Water Tank to tap stand completed with all accessories (connections, valves if necessary, Nipple, elbows etc.)Works include pipelaying, backfilling of pipeline trench, pipeline testing, and commissioning of works. All works to be done according to the specifications and site supervisors instructions. | Ml | 600 | 330 |  |  | 0
توريد وتركيب مواسير بولي اثلين قطر 2 انش وضغط 10 بار من الخزان العلوي نقطة توزيع الحنفيات والعمل يشمل جميع الملحقات (التوصيلات والصمامات إذا لزم الأمر ، و النيبلات ، والاكواع ، والموزعات ، والتحويلات ، وما إلى ذلك ، وتشمل التركيب واختبار الضغط ، حسب المواصفات والتعليمات الموضحة وتعليمات المهندس المشرف.
4.4 | Provide and lay Polyethylene Pipes 2" 10 bar from the Elevated Water Tank to Health Facility complete with all accessories (connections, valves if necessary, Nablatt, elbows etc)Works includes installation,testing,backfilling and commissioning,all in accordance to the specifications and instructions of the supervising engineer. | Ml | 600 | 330 |  |  | 0
توريد وتركيب مواسير بولي اثلين قطر2 انش من الخزان العلوي الى المركز الصحي والعمل يشمل جميع الملحقات (التوصيلات والصمامات إذا لزم الأمر ، والنيبلات ، والاكواع ، والموزعات ، والتحويلات ، وما إلى ذلك ، وتشمل التركيب واختبار الضغط ، حسب المواصفات والتعليمات الموضحة وتعليمات المهندس المشرف.
4.6 | Supply and install bulk water flow meter 2 inch Dia.at well to measure water flow from well | No. | 2
توريد وتركيب عدادات المياه قطر 2 بوصة عند البئر ,والخزان لقياس تدفق المياه من البئر
4.7 | Supply and install check valve 2 inch Dia. At the well raising main | No. | 1
توريد و تركيب محبس عدم الرجوع قطر 2 بوصه عند خط الضخ الرئيسي من البئر
4.8 | Supply fiiting and extent connection from 2" pipe line to 1" openning of existing 2 m3 tiga tank | Service | 1
توريد و عمل وصلة لخزان تيقا (2 متر مكعب) الموجود بالمركز الصحي علما بأن فتحة الخزان بقطر 1 بوصة
4.9 | Replacement of elevated tank 2", Galvanized pipe raiser and down pipe and with all fittings and other accessories and apply of new membrane(ant-rust painting) | Service | 1
تغيير المواسير القلفنايز قطر 2 بوصة النازلة و الصاعدة للخزان بأخرى جديدة مع كل الملحقات و القطع المطلوبة و عمل طلاء مقاوم للصدأ
4.1 | Supply and install gate valve 2 inch Dia. At the well raising main | No. | 4
توريد و تركيب محبس قطر2 بوصه
4.11 | Supply and install new Galavnized fittings for water elevated tank size of 2 inches (elbows, tees unions, nipples, sockets, flanches for valves) the work including also applying of water proof painting in connection joints | Service | 1
توريد و تركبيب ملحقات قلفنايز جديدة بحجم 2 بوصة و اللتي تشمل ، جلب ، يونين، نيفل و فلنشات، تيهات و أكواع
Sub Total4 | [6 empty] | 0
Grand Total cost (الإجمالي العام) | [6 empty] | #REF!
Grand Total cost Civil + Solar (الإجمالي العام) | [6 empty] | #REF!
International Rescue Committee (IRC), Sudan Program
Project Name: Lifesaving Primary Healthcare and WASH Services in Underserved Areas of Sudan
Funded by (BHA).
Intervention: Rehabilitation of Water Yard in Menza in Wd elmahi Locality, Blue Nile State

## Solar Pump (2)
جدول كميات لمشروع تأهيل محطة مياه مينزا - محلية ود الماحي. Estimation & Bill Of Quantity for Menza Water Yard Wd-elmahi Locality
Item No. | Description of work | Unit | Quantity |  | Unit cost | Total cost |  | Remark
|  |  | Contract | Executed | USD | Contract | Executed
1 | Mechanicla work الاعمال الميكانيكية
1.1 | Supply, inspect, install and operate the following item according to the technical specifications. Submersible Pump, Centrifugal multistage type, having standard ISO-9906 Specification, Pump efficiency > 70% at design point, the pump bowel (shaft, impeller, casing, pump delivery and housing, coupling, wear ring, none return valve, strainer … etc ) which made entirely from steel DIN 1.4401/AISI316. For the following type: Submersible pump: Q= 1.4L/S, H=75 m, power = 5 KW | No. | 1 | 2 |  |  | 0
1.2 | Supply, inspect, install and operate the following item according to the technical specifications. Submersible Motor (shaft end) high temp. (HT) with stainless steel (AISI 304) motor body, stainless steel splined (AISI 316 or superior) motor shaft, SS motor upper & lower, rewindable, winding PE2/PA max. temp. 50 C. water filled motors, starting DOL, voltage 380/415V, 50Hz, 3ph, motor speed > 2850 RPM, IP68, efficiency ≥ 82%, cos Ø ≥ 0.84. (NBR) rubber parts, mechanical seal sic/sic, according to DIN 24960, NEMA mounting dimensions, for the following rating : 4.5 Kw (5 HP), 2.0" or whatever rating it corresponds to Submersible pump head of 105 m. | No. | 1 | 330 |  |  | 0
1.3 | Supply of Gl ( raisers ) pipes, square threaded from both sides, 3meter length, Class b (medium), 3.25 mm thickness,3.61 kg/m. the fittings from carbon steel or stainless steel, working pressure rating ( 35 kg/cm2 ) with all the accessories of flanges, seals for the following nominal size:-1.5" with connect to the pump and pumping pipes 2" iron . | NO | 13 | 1 |  |  | 0
1.4 | Provide and install water meter with all needed accessories 2.0" | NO | 1 | 1 |  |  | 0
1.5 | Provide and install Heavy duty approved surface plate ( ملزمه ), fabricated of steel with at Suitable for pipe diameter ( 32mm thick ), rigidly support the total weight of motor, pump, pipes, cables .. etc. | NO | 1 | 1 |  |  | 0
1.6 | Supply and install new Generator, chienese type, water cooled with following specifications: 1. 18 HP power 2. Diesel Fuel 3. Single cylinder 4. 230 V, 43.5 A, 3 phase, 50 Hz the work include fixing the generator in steel mounting structre and provding cooling system | pcs | 1 | 700
Sub Total | [6 empty] | 0
2 | Electrical work الاعمال الكهربائية
2.1 | Supply, inspect, install and operate the following item according to the technical specifications. ( PV solar Panels ):- 300 w - The panels should be mono or poly crystalline. - Should be class A, fire class C, (72) cell. - 1000 Vdc ( -40 to +85ْ C ) operating temp. - Mechanical pressure not less than 5400 Pascal. - Panels shall comply with IEC 61215, IEC 61730, UL 1703 Standards. | No. | 22 | 2 |  |  | 0
2.2 | Supply, inspect, install and operate the following item according to the technical specifications. ( Solar Pump controller ( Inverter ):- 5 kw - MPPT type, ( 400 – 800 Vdc ). - It has a variable frequency, ( 0 – 50 Hz ). - It has DC input & AC output . - Output voltage 380/415 Vac. - Protection grade not less than IP54. - Comply with IEC 80529, UL 508C, EN 50178. | No. | 1 | 330 |  |  | 0
2.3 | Supply, inspect, install and operate the following item according to the technical specifications. Combiner Box :- 4 strings box - Box made of Iron insulated epoxy layer . - Protection type IP54, with SPD device. - Wall mounting feature. - Rating voltage 1000 DCV. - Contains fuse holders ( 5 Amp rating ). - Equipped with DC- disconnector switch 160A. - Contains bypass and blocking protection. - Temp range : 10ْ C to 55ْ C | No. | 1 | 330 |  |  | 0
2.4 | Supply, inspect, install and operate the following item according to the technical specifications. Submersible electrical cable, finely stranded copper conductor copper double insulated sheath material (EPR/EPDM), core insulation (EPR/EPDM), up to 90 C ,current carrying capacity (DIN/VDE 298-4) normal voltage (450/750V – 0.6/ 1KV), class 5 lexibility, water resistant. special for drinking water .Standards (IEC 245, IEC 228, DIN 7295, VDE 250 VDE 282, VDE 293, VDE 295). For the following :-4X8 mm2 | M | 100 | 330 |  |  | 0
2.5 | Supply, inspect, install and operate the following item according to the technical specifications. DC / AC Switch :- - Manual DC/AC switch, 4 – poles change over switch ( or 6 – pole change over switch ). - The box made of iron insulated epoxy IP54. - 2 inputs, and 1 output. - Wall mounting . | No. | 1
2.6 | Supply, inspect, install and operate all the following items according to the technical specifications. DC cables :- - Solar copper cable twin core 2×4mm2, (PVC insulated, cu cables positive and negative). - Cable to connect each solar panel arrage to the combiner box. - Flexible , double isolation and voltage drop should not exceed 3% . DC cables shall be according to the standard TUV & UL system, shall have a voltage not less than 800 DCV . | M | 30 | 330 |  |  | 0
2.7 | Supply, inspect, install and operate the following item according to the technical specifications. Electrical control Panel (Starter):- 3phase, 415 V ±10 % , 50Hz , mainly design to work as an Auto transformer starter, provided with electronic monitoring and protection unit. The whole electrical parts designed according to VDE/DIN standards requirements and regulations , for the following rating :- 3 KW Panel.. | No. | 1 | 330 |  |  | 0
2.8 | Supply, inspect, install and operate the following item according to the technical specifications. Grounding and lighting system :- - Grounding system for each set of panels and other system components & panels. - Lighting arrester to protect all components and equipment. | LS | 1 | 330 |  |  | 0
Sub Total | [6 empty] | 0
3 | Civil work الاعمال الانشائية
3.1 | rovision and installation of steel net (fence) around the Solar panel, area of 20x20 m2 and 2m using chain link rools and 2 inch iron angel thichness of 3mm, fixed to the ground with concrete base ( 40cm x 40cm) , and mix of 1:1.5:3 including preparation, placing, compaction and curing using ordinary Portland Cement , and 15 cm depth. as per attached drawing and engineer instructions | Ml | 60 | 2 |  |  | 0
3.2 | Provide and install gate with dimensions 2*3 of arch mesh wire with diameter of the iron 1.5 inch,to be X-letter shaped and installed on the two tracks of 3 inches.All works to be executed in accordance to the site engineers instructions. | No | 1
3.3 | Supply, inspect, install and operate the following item according to the technical specifications. Frames and Bases and mounting steel structures for solar panels, from I beams & U beams ( 80× 40mm ) posts, squire pipes 4x8 cm thickness of 1.8 mm and bolts and ruts and any other accessories, each string carry from 3.5 KW to 4 KW and Instilled ground by four reinforced concrete bases (100 cm X 50 cm X 50 cm). | Service | 1 | 330 |  |  | 0
3.4 | Supply an laydown Selected Material as base lyer for solar system area and elevated water tank area with good compaction, and thickness of 10 cm | m3 | 30
| rovision and installation of steel net (fence) around the Elevated tank, area of 10x10 m2 and 2m using chain link rools and 2 inch iron angel thichness of 3mm, fixed to the ground with concrete base ( 40cm x 40cm) , and mix of 1:1.5:3 including preparation, placing, compaction and curing using ordinary Portland Cement , and 15 cm depth. as per attached drawing and engineer instructions | Ml | 40 | 2
3.5 | Supply and install Sign board for visibility with tube 10x10cm thick 3mm , and plate in the top with IRC logo design 2mm 2 sides , with reinforced concrete bases 60x60x60cm,total height from GL to be 2 meter using tube 10x10cm thickness 3 mm , including a support as per the drawing.Plate to be of 1.2m width,60cm height,3mm thick as shown in the photo. one side to be painted with two layers of rust-resitant paint,and IRC logo written with original color of the IRC logos,or equivalent sticker which must be sun-resistant. | No. | 1
Sub Total | [6 empty] | #REF!
4 | Building capacity for Water Yard operators
4.1 | Conduct training of operating and management of water yard for water yard selected operatos and water management committee | Service | 1 | 200
Sub Total9
Grand Total cost (الإجمالي العام) | [6 empty] | #REF!
International Rescue Committee (IRC), Sudan Program
Project Name: Lifesaving Primary Healthcare and WASH Services in Underserved Areas of Sudan
Funded by (BHA).
Intervention: Rehabilitation of Water Yard in Menza in Wd elmahi Locality, Blue Nile State

## Distibution points
جدول كميات لمشروع تأهيل محطة مياه مينزا - محلية ود الماحي. Estimation & Bill Of Quantity for Menza Water Yard Wd-elmahi Locality
Item No. | Description of work | Unit | Quantity | Unit cost | Total cost | Remark
|  |  | Contract | USD | Contract
1 | Rehabilitation of water collection point إعادة تأهيل نقطة توزيع المياه
1.1 | Provide and paint to all walls of the distribution water station using Plastic paint (glossy) of good quality and in two layers of anti-humidity white color paint | m2 | 9.5
توريد و طلاء جميع الجدران الخارجية لنقطة توزيع المياه بطلاء بلاستيكي جيد الجودة مقاوم طبقتين لون كريمي شاملا كل ما يلزم لإنهاء العمل على أكمل وجه حسب المواصفات و تعليمات المهندس المشرف
1.2 | Supply and install push or lockable taps of high quality stainless steel size of 1" | No. | 7
توريد وتركيب حنفية جدار حديدية صناعة ممتازة غير قابلة للصدأ
1.3 | Supply and install of flange coupling ,Ball valve 1.5 inch, (Metal seat), Ductile Iron , work includes any materials or activities necessary for install and operate, and all necessary to complete the work according to Specifications and the instructions of Engineer. | No. | 1
توريد وتركيب محبس يد عالي التحمل ضغط التشغيل له لا يقل عن 25 كجم/سم مربع قطر 1.5هنش والعمل يشمل جميع ما يلزم من قطع خاصة وتوصيلات لإكمال العمل بحسب المواصفات وتعليمات المهندس المشرف
1.4 | Supply and installation of 2'' Galavanized Water pipe 3mm thichness to replace the old pipe | No. | 1
توريد و تركيب ماسورة 2 بوصة قلفنايز بسمك 3 ملم واستبدال الماسورة القديمة في نقطة توزيع الحنفيات
1.5 | install of new animal trough collection point with capacity of 1 m3 using MS plate 3 mm thickness , the work include setup of stand pipe 63 mm (2") with valve, elbow, nipple and any other fitting near the fence and then to be extended to animal trough outside the fence using flexible HDPE pipe | No. | 1
توريد و تركيب نقطة تجميع حوض حيوانات جديدة بسعة 1 م 3 باستخدام لوحة MS بسمك 3 مم ، ويشمل العمل تركيب أنبوب حامل 63 مم (2 بوصة) مع صمام وكوع وأي ملحقات أخرى بالقرب من السياج ثم يتم تمديدها إلى حوض الحيوانات خارج السياج باستخدام أنابيب HDPE المرنة بحجم 2 بوصة .
1.6 | Rehabilitation manhole with dimensions of (70cm x 70cm x 50cm) , with steel cover of 2mm thickness and work include internal and external plastering and painting with yellow color and supply new lock. | No. | 2
توريد و صيانة غرف تفتيش بأبعاد صافي ( 50سم * 70سم * 70سم ) سم مع اغطيه حديدية صفائح محببة سماكة 2مم والعمل يشمل التلبيس من الداخل والخارج والطلاء بلون اصفر و توريد قفل حديدي .
1.7 | conduct outside/inside inspection and repair of water elevated tank for any holes, rust or any other damages, the work include also applying of water proof | Service | 1
إجراء فحص خارجي / داخلي وإصلاح خزان الماء المرتفع بحثًا عن أي ثقوب أو صدأ أو أي أضرار أخرى ، ويشمل العمل أيضًا تطبيق طلاء مقاوم للماء و الصداء للبرج مع استحدام دهانات من اجود الأنواع حسب توجيه المهندس المشرف
Water Point
2 | Excavation works of drainage pit حفرة التصريف
2.1 | Excavate for drainage pit measuring 1m x 1m x 0.5m depth as shown in drawings, and according to the supervisor's instructions. | M3 | 0.5
اعمال الحفر لحفرة التصريف 1متر *1متر *0.5 متر عمق بحسب الرسومات وتعليمات المهندس المشرف.
2.2 | excavation of drainage trench length of 8 meters minimum, width of 30 cm and depth of 15 cm to drain excessed water from tab stand | Ml | 10
حفر و عمل مجرى تصريف بطول 10 أمتار و عرض 30 سم و عمق 15 سم لتصريف المياه الفائضة من نقطة مياه الحنفيات الى حوض التصريف
Sub Total5
Sub Total (1 Water Collection Point)
International Rescue Committee (IRC), Sudan Program
Project Name: Lifesaving Primary Healthcare and WASH Services in Underserved Areas of Sudan
Funded by (BHA).
Intervention: Rehabilitation of Water Yard in Menza in Wd elmahi Locality, Blue Nile State