## Civil works.
جدول كميات لمشروع تأهيل محطة مياه منجلنغ - محلية ود الماحي . Estimation & Bill Of Quantity for Menchaling Mini Water Yard Wd elmahi Locality | [8 empty] | 578
Item No. | Description of work | Unit | Quantity |  | Unit cost | Total cost |  | Remark
|  |  | Contract | Executed | USD | Contract | Executed
1 | Site Preparations أعمال تجهيز الموقع
1.1 | prepare the site and clean it from rubbish, Debris or any unwanted items. | m2 | 400 | 330 |  |  | 0
تنظيف الموقع من الأوساخ و الأنقاض أو أي مواد غير مرغوب فيها و إزالتها بعيدا من الموقع
1.2 | Transportation of all work personnel, equipment's and material to the site. | L.S | 1 | 2 |  |  | 0
ترحيل المواد و الآليات و المعدات و فريق العمل الى الموقع
2 | Construction of Elevated Water Tank for Water distribution بناء خزان مياه مرتفع
2.1 | Supply and install material for Construction and fabrication of Water Elevated tank tower and plastic tank as Annex1 | L.S | 1 | 2 |  |  | 0
توريد وتركيب المواد اللازمة لبناء وتصنيع برج لخزان المياه والخزان البلاستيكي كما في الملحق 1
Sub Total 2 (1 Water Collection Point) | [5 empty] | 0 | 0
3 | Rehabilitation of water collection point بناء نقاط توزيع المياه
3.1 | Supply and install material for rehabilitation collection Water points as Annex2 | L.S | 1 | 2 |  |  | 0
توريد مواد لإعادة تأهيل نقاط مياه بكافة ملحقاتها بحسب الملحق 2
Sub Total 3 (1 Water Collection Point) | [5 empty] | 0 | 0
4 | Pipeline work اعمال شبكة المياه
4.1 | install 2" material for borehole water point collecttion (Gl Pipe,elbows, teflontapes,check valve, flange adpators and any orher accessories) and as per engineer instructions | L.S | 1
توريد مواد (ماسورة قلفنايز 2 بوصة، أكواع قلفنايز 2 بوصة، فلنشات و أدابترات) و عمل توصيلة للبئر مع عمل كل ما يلزم من أصول الصنعة
4.2 | Supply and install bulk water flow meter 1.25 inch Dia.at well to measure water flow from well | No. | 2
توريد وتركيب عدادات المياه قطر 1.25 بوصة عند البئر ,والخزان لقياس تدفق المياه من البئر
Sub Total4 | [5 empty] | 0 | #REF!
Grand Total cost (الإجمالي العام) | [5 empty] | 0 | #REF!
Grand Total cost Civil + Solar (الإجمالي العام) | [5 empty] | 0 | #REF!
International Rescue Committee (IRC), Sudan Program
Project Name: Lifesaving Primary Healthcare and WASH Services in Underserved Areas of Sudan
Funded by (BHA).
Intervention: Upgrading of Hand Pump in Menchaling in Wd elmahi Locality, Blue Nile State

## Solar Pump
جدول كميات لمشروع تأهيل محطة مياه منجلنغ - محلية ود الماحي . Estimation & Bill Of Quantity for Menchaling Mini Water Yard Wd elmahi Locality
Item No. | Description of work | Unit | Quantity | Unit cost | Total cost |  | Remark
|  |  | Contract | USD | Contract | Executed
1 | Mechanicla work الاعمال الميكانيكية
1.1 | Supply, inspect, install and operate the following item according to the technical specifications. Submersible Pump, Centrifugal multistage type, having standard ISO-9906 Specification, Pump efficiency > 70% at design point, the pump bowel (shaft, impeller, casing, pump delivery and housing, coupling, wear ring, none return valve, strainer … etc. ) which made entirely from steel DIN 1.4401/AISI316. For the following type: Submersible pump: Q= 2.1 m3/hr , H=75 m | No. | 1 |  |  | #REF! |  | 1.3889
1.2 | Supply, inspect, install and operate the following item according to the technical specifications. Submersible Motor (shaft end) high temp. (HT) with stainless steel (AISI 304) motor body, stainless steel splined (AISI 316 or superior) motor shaft, SS motor upper & lower, rewindable, winding PE2/PA max. temp. 50 C. water filled motors, starting DOL, voltage 380/415V, 50Hz, 3phases, motor speed > 2850 RPM, IP68, efficiency ≥ 82%, cos Ø ≥ 0.84. (NBR) rubber parts, mechanical seal sic/sic, according to DIN 24960, NEMA mounting dimensions, for the following rating : 1 Kw , 1.25" or whatever rating it corresponds to Submersible pump . | No. | 1 |  |  | #REF!
1.3 | Supply and install 1 inch poly ethelyen hose pipe, presure of 6 bar | ML | 45 |  |  | #REF!
1.4 | Provide and install Heavy duty approved surface plate ( ملزمه ), fabricated of steel with at Suitable for pipe diameter ( 32mm thick ), rigidly support the total weight of motor, pump, pipes, cables .. etc. | NO | 1 |  |  | #REF!
Sub Total7 |  |  |  |  | 0 | #REF!
2 | Electrical work الاعمال الكهربائية
2.1 | Supply, inspect, install and operate the following item according to the technical specifications. ( PV solar Panels ):- 405 watts - The panels should be mono or poly crystalline. - Should be class A, fire class C, (72) cell. - 1000 Vdc ( -40 to +85ْ C ) operating temp. - Mechanical pressure not less than 5400 Pascal. - Panels shall comply with IEC 61215, IEC 61730, UL 1703 Standards. | No. | 3 |  |  | #REF!
2.2 | Supply, inspect, install and operate the following item according to the technical specifications. ( Solar Pump controller ( Inverter ):- 1 kw - MPPT type, ( 400 – 800 Vdc ). - It has a variable frequency, ( 0 – 50 Hz ). - It has DC input & AC output . - Output voltage 380/415 Vac. - Protection grade not less than IP54. - Comply with IEC 80529, UL 508C, EN 50178. | No. | 1 |  |  | #REF!
2.3 | Supply, inspect, install and operate the following item according to the technical specifications. Submersible electrical cable, finely stranded copper conductor copper double insulated sheath material (EPR/EPDM), core insulation (EPR/EPDM), up to 90 C ,current carrying capacity (DIN/VDE 298-4) normal voltage (450/750V – 0.6/ 1KV), class 5 flexibility, water resistant. special for drinking water .Standards (IEC 245, IEC 228, DIN 7295, VDE 250 VDE 282, VDE 293, VDE 295). For the following :-4X8 mm2 | M | 100 |  |  | #REF!
2.4 | Supply, inspect, install and operate the following item according to the technical specifications. DC / AC Switch :- - Manual DC/AC switch, 4 – poles change over switch ( or 6 – pole change over switch ). - The box made of iron insulated epoxy IP54. - 2 inputs, and 1 output. - Wall mounting . | No. | 1
2.5 | Supply, inspect, install and operate all the following items according to the technical specifications. DC cables :- - Solar copper cable twin core 2×8mm2, (PVC insulated, cu cables positive and negative). - Cable to connect each solar panel arrange to the combiner box. - Flexible , double isolation and voltage drop should not exceed 3% . DC cables shall be according to the standard TUV & UL system, shall have a voltage not less than 800 DCV . | M | 50 |  |  | #REF!
2.7 | Supply, inspect, install and operate the following item according to the technical specifications. Electrical control Panel (Starter):- 3phase, 415 V ±10 % , 50Hz , mainly design to work as an Auto transformer starter, provided with electronic monitoring and protection unit. The whole electrical parts designed according to VDE/DIN standards requirements and regulations , for the following rating :- 10 KW Panel.. | No. | 1 |  |  | #REF!
2.8 | Supply, inspect, install and operate the following item according to the technical specifications. Grounding and lighting system :- - Grounding system for each set of panels and other system components & panels. - Lighting arrester to protect all components and equipment. | LS | 1 |  |  | #REF!
Sub Total8 |  |  |  |  | 0 | #REF!
3 | Civil work الاعمال الانشائية
3.1 | Provision and installation of fence wire (Gabion ) around the water yard, area of 20x20 m2 and 2m using chain link rools and 2 inch iron angel thichness of 3mm, 7x7 cm fixed to the ground with concrete base ( 40cm x 40cm) , and mix of 1:1.5:3 including preparation, placing, compaction and curing using ordinary Portland Cement , and 15 cm depth. as per attached drawing and engineer instructions | Ml | 80 |  |  | 0
3.2 | Provide and install gate with dimensions 2*3 of arch mesh wire with diameter of the iron 1.5 inch, to be X-letter shaped and installed on the two tracks of 3 inches. All works to be executed in accordance to the site engineers instructions. | No | 1 |  |  | 0
3.3 | Supply and install Sign board for visibility with tube 10x10cm thick 3mm , and plate in the top with IRC logo design 2mm 2 sides , with reinforced concrete bases 60x60x60cm,total height from GL to be 3 meter using tube 10x10cm thickness 3 mm , including a support a.Plate to be of 1.2m width,60cm height,3mm thick a. one side to be painted with two layers of rust-resitant paint,and IRC logo written with original color of the IRC & USAID logos,or equivalent sticker which must be sun-resistant. | No. | 1
Sub Total9 |  |  |  |  | 0 | #REF!
4 | Building capacity for Water Yard operators
4.1 | Conduct training of operating and management of water yard for water yard selected operatos and water management committee | Service | 1
Sub Total9 |  |  |  |  | 0 | #REF!
Grand Total cost (الإجمالي العام) |  |  |  |  | 0 | #REF!
International Rescue Committee (IRC), Sudan Program
Project Name: Lifesaving Primary Healthcare and WASH Services in Underserved Areas of Sudan
Funded by (BHA).
Intervention: Upgrading of Handpump in Mencalang in Wed-elmahi Locality, Blue Nile State

## Elevated Tank
جدول كميات لمشروع تأهيل محطة مياه منجلنغ - محلية ود الماحي . Estimation & Bill Of Quantity for Menchaling Mini Water Yard Wd elmahi Locality
Item No. | Description of work | Unit | Quantity | Unit cost | Total cost | Remark
|  |  | Contract | USD | Contract
1 | Rehabilitation of water collection point إعادة تأهيل نقطة توزيع المياه
1.1 | Supply and install 1 No of PVC (plastic tank) Vertical and cylinder shape with capacity of 5000 liter, Interior surface painted with black water roofing painting with all Accessories and fitting , tiga brand is favorable | Tank | 1
توريد و تركيب خزان بلاستيكي (نوعية جيدة) سعة 5000 لتر ذو شكل إسطواني و إتجاه رأسي بكامل ملحقاته مع مراعاة ان يكون السطح الداخلي اسود اللون
1.2 | supply material (Steel, Iron angels) to fabricate 4 meter high tower to holds the elevated tank using heavy wight material and apply 2 coat painting with epoxy painting or any type of unti-rust painting for any as explained in technical specifications and as per Engineer instructions | Service | 1
| توريد و تصنيع مواد (حديد ، زوايا ز صفائح) برج بارتفاع 4 أمتار لحمل الخزان البلاستيكي باستخدام مادة ثقيلة الوزن مع طلاء طبقتين بطلاء إيبوكسي أو أي نوع من الطلاء المقاوم للصدأ لأي منها كما هو موضح في المواصفات الفنية وحسب تعليمات المهندس |  | 1
1.3 | Supply materials and fabricate mounting structre for 405 watt PV Solar at the top of elevated tank with all accessories as per engineer structr | pcs | 3
توريد مواد و تركيب جسم حامل لالواح الطاقة الشمسية بحجم 405 واط
1.4 | Fabricate and Install a metal ladder and handrail to reach the platform as explained in specification and as per engineer Instructions | Service | 1
| صنيع وتركيب سلم معدني و درابزين للوصول إلى شكل اللوحة كما هو موضح في المواصفات ووفقًا لتعليمات المهندس. |  | 1
1.5 | Supply material and cast reinforced concrete for tower foundation using mix of 1:2:4 and 12 mm bars and BRC wire mesh for foundation slab as per drawing and as per engineer instructions | M3 | 1.5
| توريد مواد (ركام، رمل ، مياه) و عمل خرسانة مسلحة لقواعد البرج بإستخدام خلطة قياسية (1:2:4) و حديد تسليح بقطر 12 ملم ، و أيضا توريد شبكة حديد لتسليح خرسانة القاعدة حسب الرسومات و حسب توجيهات المهندس المشرف |  | 1
Subtotal 1 of Water Point |  |  |  |  | 0
International Rescue Committee (IRC), Sudan Program
Project Name: Lifesaving Primary Healthcare and WASH Services in Underserved Areas of Sudan
Funded by (BHA).
Intervention: Upgrading of Handpump in Mencalang in Wed-elmahi Locality, Blue Nile State

## Distribution points
جدول كميات لمشروع تأهيل محطة مياه منجلنغ - محلية ود الماحي . Estimation & Bill Of Quantity for Menchaling Mini Water Yard Wd elmahi Locality
Item No. | Description of work | Unit | Quantity | Unit cost | Total cost | Remark
|  |  | Contract | USD | Contract
1 | Rehabilitation of water collection point بناء نقاط توزيع المياه
1.1 | Provide Materials (bricks, sand and cement) to build water collection station ( 2m *0.8m ) and highet of 1 m. as shown in drawings ,using factory manufactured Red bricks (25cmX12cmX6cm) in 1:3 cement/sand mortar and 1.5 brick system. | m2 | 7.5
توريد و بناء نقطة توزيع حنفيات مفرغ ثقيل اتوتاميتك لبناء نقطة توزيع المياه (2م*0.8م) كما هو موضح بالرسومات باستخدام بردين مقاس 20سم*20سم*40سم بنسبة خلط للمونة الاسمنتية 1:3
1.2 | Provide cement sand plaster 13mm thick for all surfaces of distribution water point as shown in drawings . | m2 | 17
توريد مواد و عمل بياض اسمنتي اسمنتي بنسبة خلط 1:3 (سمنت/رمل) للأوجه الخارجية لنقطة توزيع المياه, والعمل يتم حسب الرسومات و المواصفات و تعليمات المهندس المشرف
1.3 | Provide and paint to all walls of the distribution water station using basematic paint (glossy) of good quality and in two layers of anti-humidity white color paint | m2 | 9.5
توريد و عمل طلاء جميع الجدران الخارجية لنقطة توزيع المياه بطلاء بلاستيكي جيد الجودة مقاوم طبقتين لون كريمي من البوماستك السلك شاملا كل ما يلزم لإنهاء العمل على أكمل وجه حسب المواصفات و تعليمات المهندس المشرف
1.4 | Supply and install push or lockable taps of high quality stainless steel size of 1" | No. | 5
توريد وتركيب حنفية جدار حديدية صناعة ممتازة غير قابلة للصدأ
1.5 | Supply and install of flange coupling ,Ball valve 1" inch, (Metal seat), Ductile Iron , | No. | 1
توريد وتركيب محبس يد عالي التحمل ضغط التشغيل له لا يقل عن 25 كجم/سم مربع قطر 1 هنش والعمل يشمل جميع ما يلزم من قطع خاصة وتوصيلات لإكمال العمل بحسب المواصفات وتعليمات المهندس المشرف
1.6 | Supply Gl pipe diameter of 1" with flanches, ball valves, union, Nevil, and any other accessories and install it instead of the old one in tap-stand water point, the work include also apply of unti-rust paint. | No. | 1
توريد و تركيب ماسورة قلفنايز بقطر 1 بوصة بنقطة توزيع الحنفيات و استبدالها مع القديمة مع تركيب الملحقات و البلوفة ،العمل يشمل عمل طلاء مقاوم للصدأ
1.7 | Supply and laydown selected material (backfill) at the area of tab stand with good compaction and thichness 10 cm | M3 | 0.5
توريد و عمل ردميات في منطقة حنفيات ترش و تمندل جيدا بسمك 10 سم
1.8 | install of new animal trough collection point with capacity of 1 m3 using MS plate 3 mm thickness , the work include setup of stand pipe 63 mm (2") with valve, elbow, nipple and any other fitting near the fence and then to be extended to animal trough outside the fence using flexible HDPE pipe | No. | 1
توريد و تركيب نقطة تجميع حوض حيوانات جديدة بسعة 1 م 3 باستخدام لوحة MS بسمك 3 مم ، ويشمل العمل تركيب أنبوب حامل 63 مم (2 بوصة) مع صمام وكوع وأي ملحقات أخرى بالقرب من السياج ثم يتم تمديدها إلى حوض الحيوانات خارج السياج باستخدام أنابيب HDPE المرنة بحجم 2 بوصة .
1.9 | supply material and cast plain concrete with mix of 1:3:6 for the base of animal trough and donkey cart collection point | Service | 0.642
توريد و صب خرسانة عادية بإسمنت عادي تحت الحوض بسماكة 10سم مع الدمك و رش الماء و الصب باستخدام اسمنت بوتلاندي عادي 250كجم/متر3
Subtotal 1 of Water Point
2 | Excavation works of drainage pit حفرة التصريف
2.1 | Excavate for drainage pit measuring 1m x 1m x 0.5m depth as shown in drawings, and according to the supervisor's instructions. | M3 | 0.5
اعمال الحفر لحفرة التصريف 1متر *1متر *0.5 متر عمق بحسب الرسومات وتعليمات المهندس المشرف.
2.2 | Excavate trench to drain water from tap stand 0.3 m wide and 0.1 m depth and 7 meter long with concrete lining | Ml | 10
حفر و عمل مجرى تصريف بطول 10 أمتار و عرض 30 سم و عمق 15 سم لتصريف المياه الفائضة من نقطة مياه الحنفيات الى حوض التصريف
Sub Total 2
Sub Total (1 Water Collection Point) |  |  |  |  | 0
International Rescue Committee (IRC), Sudan Program
Project Name: Lifesaving Primary Healthcare and WASH Services in Underserved Areas of Sudan
Funded by (BHA).
Intervention: Upgrading of Handpump in Mencalang in Wed-elmahi Locality, Blue Nile State