## Civil works.
جدول كميات لمشروع تأهيل محطة مياه القري - محلية الروصيرص . Estimation & Bill Of Quantity for Al Garri Water Yard Ar-rusaires Locality
Item No. | Description of work | Unit | Quantity |  | Unit cost | Total cost |  | Remark
|  |  | Contract | Executed | USD | Contract | Executed
1 | Site Preprations أعمال تجهيز الموقع
1.1 | prepare the site and clean it from rubbish, Debries or any unwanted items. | service | 600 | 330 |  |  | 0
تنظيف الموقع من الأوساخ و الأنقاض أو أي مواد غير مرغوب فيها و إزالتها بعيدا من الموقع
1.2 | Transportation of all work personnel, equipments and material to the site. | L.S | 1 | 2 |  |  | 0
ترحيل المواد و الآليات و المعدات و فريق العمل الى الموقع
1.3 | Supply and laydown selected material (backfill) at the area of water yard with good compaction and thichness 10 cm | M3 | 35
توريد و عمل ردميات في منطقة حنفيات ترش و تمندل جيدا بسمك 10 سم
Sub Total1 | [6 empty] | 0
2 | Rehabilitation of water collection point إعادة تأهيل نقاط توزيع المياه
2.1 | Supply and install material for rehabilitation collection Water points as Annex2 | L.S | 1 | 2 |  |  | 0
توريد مواد لإعادة تأهيل نقاط مياة بكافة ملحقاتها بحسب الملحق 2
Sub Total 2 (1 Water Collection Point) | [5 empty] | 0 | 0
4 | Pipeline work اعمال شبكة المياه
4.1 | Excavation for pipeline trench depth 60cm and width total distance 50m from the water well to the Elevated Water Tank.All works to be done according to the specifications and instructions of the supervisor. | Ml | 500 | 330 |  |  | 0
أعمال الحفر والردم لخط الأنابيب من البئر الى الخزان العلوي بعمق 50 سم مع تسوية الحفر بطبقة من التربة الناعمة أسفل الأنبوب ، والردم باستخدام تربة صالحة مع الرش والدك بعد الردم ، وفقا للمواصفات ، والتعليمات الموضحة ، وتعليمات المهندس المشرف
4.2 | Provide and lay Polyethylene Pipes 2" 10 bar in pipeline trench from the well to the Elevated tank completed with all accessories (connections, valves if necessary, Nablatt, elbows etc)Works include pipelaying,backfilling of pipeline trench,pipeline testing,and commissioning of works.All works to be done according to the specifications and site supervisors instructions. | Ml | 500 | 330 |  |  | 0
توريد وتركيب مواسير بولي اثلين قطر 2 انش وضغط 10 بار من البئر الى الى الخزان العلوي والعمل يشمل جميع الملحقات (التوصيلات والصمامات إذا لزم الأمر ، والنيبلات ، والاكواع ، والموزعات ، والتحويلات ، وما إلى ذلك ، وتشمل التركيب واختبار الضغط ، حسب المواصفات والتعليمات الموضحة وتعليمات المهندس المشرف.
4.3 | Supply materials and construct valve inspection chamber size 0.8 x 0.8 cm with solid blocks and concrete with cover granular thickness 1.5 mm with hinged frame and locks. Cover to be protected with three coats of anti-rust paint,and all works to be completed to the satisfaction of the site supervisor. | No. | 2 | 330 |  |  | 0
بناءغرفة التفتيش بابعاد 0.8 × 0.8 سم من البلك الصم مع عمل غطاء حديد محبب بسمك 1.5 ملم مع الإطار والأقفال والمفصلات مع طلاء ثلاثة وجوه ملونة لتجنب الرطوبة والغبار وكل ما يلزم
4.4 | Supply fiiting and extent connection from 2" pipe line to 1" openning of existing 2 m3 tiga tank | Service | 1
عمل وصلة لخزان تيقا (2 متر مكعب) الموجود بالمركز الصحي علما بأن فتحة الخزان بقطر 1 بوصة
4.5 | Supply and install bulk water flow meter 2 inch Dia.at well to measure water flow from well | No. | 2
توريد وتركيب عدادات المياه قطر 2 بوصة عند البئر ,والخزان لقياس تدفق المياه من البئر
4.6 | Replacement of elevated tank 2", Galvanized pipe raiser and down pipe and with all fittings and other accessories and apply of new membrane(ant-rust painting) | Service | 1
تغيير المواسير القلفنايز قطر 2 بوصة النازلة و الصاعدة للخزان بأخرى جديدة مع كل الملحقات و القطع المطلوبة و عمل طلاء مقاوم للصدأ
4.7 | Supply and install new Galavnized fittings for water elevated tank size of 2 inches (elbows, tees unions, nipples, sockets, flanches for valves) the work including also applying of water proof painting in connection joints | Service | 1
توريد و تركبيب ملحقات قلفنايز جديدة بحجم 2 بوصة و اللتي تشمل جلب ، يونين، نيفل و فلنشات، تيهات و أكواع
Sub Total4 | [6 empty] | 0
Grand Total cost (الإجمالي العام) | [6 empty] | #REF!
Grand Total cost Civil + Solar (الإجمالي العام) | [5 empty] | 0 | #REF!
International Rescue Committee (IRC), Sudan Program
Project Name: Lifesaving Primary Healthcare and WASH Services in Underserved Areas of Sudan
Funded by (BHA).
Intervention: Rehabilitation of Water Yard in Al Garri in Ar-rusaires Locality, Blue Nile State

## Solar Pump
جدول كميات لمشروع تأهيل محطة مياه القري - محلية ود الروصيرص. Estimation & Bill Of Quantity for al Garri Water Yard Ar-rusaires Locality
Item No. | Description of work | Unit | Quantity | Unit cost | Total cost |  | Remark
|  |  | Contract | USD | Contract | Executed
1 | Mechanicla work الاعمال الميكانيكية
1.1 | Supply, inspect, install and operate the following item according to the technical specifications. Submersible Pump, Centrifugal multistage type, having standard ISO-9906 Specification, Pump efficiency > 70% at design point, the pump bowel (shaft, impeller, casing, pump delivery and housing, coupling, wear ring, none return valve, strainer … etc ) which made entirely from steel DIN 1.4401/AISI316. For the following type: Submersible pump: Q= 1.4L/S, H=75 m, power = 2.2 KW | No. | 1 |  |  | #REF! |  | 1.3889
1.2 | Supply, inspect, install and operate the following item according to the technical specifications. Submersible Motor (shaft end) high temp. (HT) with stainless steel (AISI 304) motor body, stainless steel splined (AISI 316 or superior) motor shaft, SS motor upper & lower, rewindable, winding PE2/PA max. temp. 50 C. water filled motors, starting DOL, voltage 380/415V, 50Hz, 3ph, motor speed > 2850 RPM, IP68, efficiency ≥ 82%, cos Ø ≥ 0.84. (NBR) rubber parts, mechanical seal sic/sic, according to DIN 24960, NEMA mounting dimensions, for the following rating : 2.2 Kw , 1.25" or whatever rating it corresponds to Submersible pump . | No. | 1 |  |  | #REF!
1.3 | Supply of Gl ( raisers ) pipes, square threaded from both sides, 3meter length, Class b (medium), 3.25 mm thickness,3.61 kg/m. the fittings from carbon steel or stainless steel, working pressure rating ( 35 kg/cm2 ) with all the accessories of flanges, seals for the following nominal size:-1.25" with connect to the pump and pumping pipes 2" iron . | NO | 13 |  |  | #REF!
1.4 | Provide and install Check valve ( Non Return valves ) flanges dimensions to EN 1092-2, inside and outside epoxy – coated, colour blue, shaft bearings made of bronze, body, bonnet ( Ductile Iron ), PN (16) for vertical and horizontal installation.DN ( 53mm ),2.0" | No. | 1 |  |  | #REF!
1.5 | Provide and install Gate Valve ( Internal dial and external blue two pack epoxy ), PN (16), face to face according to EN 558 or equivalent , standard flange drilling to EN 1092-2 ( ISO 7005-2 ) or equivalent, working pressure 25 bar, hand wheel, body, bonnet & wedge ( Ductile iron ), O-rings and gasket ( EPDM ), stem, fasteners ( stainless steel ). | No. | 3
1.6 | Provide and install Heavy duty approved surface plate ( ملزمه ), fabricated of steel with at Suitable for pipe diameter ( 32mm thick ), rigidly support the total weight of motor, pump, pipes, cables .. etc. | NO | 1 |  |  | #REF!
Sub Total7 | [5 empty] | #REF!
2 | Electrical work الاعمال الكهربائية
2.1 | Supply, inspect, install and operate the following item according to the technical specifications. ( PV solar Panels ):- 320 w - The panels should be mono or poly crystalline. - Should be class A, fire class C, (72) cell. - 1000 Vdc ( -40 to +85ْ C ) operating temp. - Mechanical pressure not less than 5400 Pascal. - Panels shall comply with IEC 61215, IEC 61730, UL 1703 Standards. | No. | 10 |  |  | #REF!
2.2 | Supply, inspect, install and operate the following item according to the technical specifications. ( Solar Pump controller ( Inverter ):- 2.2 kw. - It has a variable frequency, ( 0 – 50 Hz ). - It has DC input & AC output . - Output voltage 380/415 Vac. - Protection grade not less than IP54. - Comply with IEC 80529, UL 508C, EN 50178. | No. | 1 |  |  | #REF!
2.3 | Supply, inspect, install and operate the following item according to the technical specifications. Combiner Box :- 4 strings box - Box made of Iron insulated epoxy layer . - Protection type IP54, with SPD device. - Wall mounting feature. - Rating voltage 1000 DCV. - Contains fuse holders ( 5 Amp rating ). - Equipped with DC- disconnector switch 160A. - Contains bypass and blocking protection. - Temp range : 10ْ C to 55ْ C | No. | 1 |  |  | #REF!
2.4 | Supply, inspect, install and operate the following item according to the technical specifications. Submersible electrical cable, finely stranded copper conductor copper double insulated sheath material (EPR/EPDM), core insulation (EPR/EPDM), up to 90 C ,current carrying capacity (DIN/VDE 298-4) normal voltage (450/750V – 0.6/ 1KV), class 5 lexibility, water resistant. special for drinking water .Standards (IEC 245, IEC 228, DIN 7295, VDE 250 VDE 282, VDE 293, VDE 295). For the following :-4X8 mm2 | M | 30 |  |  | #REF!
2.5 | Supply, inspect, install and operate the following item according to the technical specifications. DC / AC Switch :- - Manual DC/AC switch, 4 – poles change over switch ( or 6 – pole change over switch ). - The box made of iron insulated epoxy IP54. - 2 inputs, and 1 output. - Wall mounting . | No. | 1
2.6 | Supply, inspect, install and operate all the following items according to the technical specifications. DC cables :- - Solar copper cable twin core 2×8mm2, (PVC insulated, cu cables positive and negative). - Cable to connect each solar panel arrage to the combiner box. - Flexible , double isolation and voltage drop should not exceed 3% . DC cables shall be according to the standard TUV & UL system, shall have a voltage not less than 800 DCV . | M | 100 |  |  | #REF!
2.7 | Supply, inspect, install and operate the following item according to the technical specifications. Electrical control Panel (Starter):- 3/single phase, 415 V ±10 % , 50Hz , mainly design to work as an Auto transformer starter, provided with electronic monitoring and protection unit. The whole electrical parts designed according to VDE/DIN standards requirements and regulations , for the following rating :- 10 KW Panel.. | No. | 1 |  |  | #REF!
2.8 | Supply, inspect, install and operate the following item according to the technical specifications. Grounding and lighting system :- - Grounding system for each set of panels and other system components & panels. - Lighting arrester to protect all components and equipment. | LS | 1 |  |  | #REF!
2.9 | Supply and install new Generator, chienese type, water cooled with following specifications: 1. 18 HP power 2. Diesel Fuel 3. Single cylinder 4. 230 V, 43.5 A, 3 phase, 50 Hz the work include fixing the generator in steel mounting structre and provding cooling system | pcs | 1
Sub Total8 | [5 empty] | #REF!
3 | Civil work الاعمال الانشائية
3.1 | supply material (iron angles, pipes, chain link) and enforce and fix the points of weakness in the fencing of water yard. | service | 1
3.2 | Supply, inspect, install and operate the following item according to the technical specifications. Frames and Bases and mounting steel structures for solar panels, from I beams & U beams ( 80× 40mm ) posts, squire pipes 4x8 cm thickness of 1.8 mm and bolts and ruts and any other accessories, each string carry from 3.5 KW to 4 KW and Instilled ground by four reinforced concrete bases (100 cm X 50 cm X 50 cm). | service | 1 |  |  | #REF!
3.3 | dismantle the old fencing and installation new of steel net (fence) around the Water yard area of 20x20 m2 and 2m using chain link rollls of good quality and 2 inch iron angel thichness of 3mm, fixed to the ground with concrete base ( 40cm x 40cm) , and mix of 1:1.5:3 including preparation, placing, compaction and curing using ordinary Portland Cement , and 15 cm depth. as per attached drawing and engineer instructions | Ml | 80 |  |  | 0
3.4 | Supply and install Sign board for visibility with tube 10x10cm thick 3mm , and plate in the top with IRC logo design 2mm 2 sides , with reinforced concrete bases 60x60x60cm,total height from GL to be 3 meter using tube 10x10cm thickness 3 mm , including a support a.Plate to be of 1.2m width,60cm height,3mm thick a. one side to be painted with two layers of rust-resitant paint,and IRC logo written with original color of the IRC & USAID logos,or equivalent sticker which must be sun-resistant. | No. | 1
Sub Total9 | [5 empty] | #REF!
4 | Building capacity for Water Yard operators
4.1 | Conduct training of operating and management of water yard for water yard selected operatos and water management committee | Service | 1
Sub Total9 | [5 empty] | #REF!
Grand Total cost (الإجمالي العام) | [5 empty] | #REF!
International Rescue Committee (IRC), Sudan Program
Project Name: Lifesaving Primary Healthcare and WASH Services in Underserved Areas of Sudan
Funded by (BHA).
Intervention: Rehabilitation of Water Yard in Garri in Ar-rusaires Locality, Blue Nile State

## Distribution Points
جدول كميات لمشروع تأهيل محطة مياه القري - محلية الروصيرص . Estimation & Bill Of Quantity for Al Garri Water Yard Ar-rusaires Locality
Item No. | Description of work | Unit | Quantity | Unit cost | Total cost | Remark
|  |  | Contract | USD | Contract
2 | Rehabilitation of water collection point إعادة تأهيل نقطة توزيع المياه
2.1 | Provide mataerial (bricks, sand and sement) and Rebuild the standing walls of tap-stand, the work inclused replastering with cement | m2 | 9.5
توريد مواد (اسمنت ، رمل و طوب ) لاصلاح و إعادة تاهيل الحوائط الساندة لمسطبة الحنفيات مع أعمال البياض
2.2 | Supply and install push or lockable taps of high quality stainless steel size of 1" | No. | 8
توريد وتركيب حنفية جدار حديدية صناعة ممتازة غير قابلة للصدأ
2.3 | Supply and install of flang coupling ,Ball valve 2 inch, (Metal seat), Ductile Iron , work includes any materials or activities necessary for install and operate, and all necessary to complete the work according to Specefications and the instructions of Engineer. | No. | 1
توريد وتركيب محبس يد عالي التحمل ضغط التشغيل له لا يقل عن 25 كجم/سم مربعقطر 2هنش والعمل يشمل جميع ما يلزم من قطع خاصة وتوصيلات لاكمال العمل بحسب المواصفات وتعليمات المهندس المشرف
2.4 | Supply Gl pipe diameter of 1.5" with flanches, ball valves, union, nevil, and any other accessories and install it instead of the old one in tap-stand water point, the work include also apply of unt-rust paint. | No. | 2
توريد و تركيب كاسورة قلفنايز بقطر 1.5 بوصة بنقطة توزيع الحنفيات و استبدالها مع القديمة مع تركيب الملحقات و البلوفة ،العمل يشمل عمل طلاء مقاوم للصدأ
2.5 | install of new donkey cart collection point, the work include setup of stand pipe 63 mm (2") with valve, elbow, nipple and any other fitting near the fence and then to be extended to collection point outside the fence using Pipe hose od 2" diameter and all accessories | Service | 1
توريد مواد (مواسير 2 بوصة ،بلوفة ،أكواع و نيفلات و أي ملحقات أخرى) بالقرب من السياج و تمديد ماسورة الى الخارج بأنبوب 2 بوصة حسب إرشادات المهندس المشرف.
2.6 | install of new animal trough collection point with capacity of 1 m3 using MS plate 3 mm thickness , the work include setup of stand pipe 63 mm (2") with valve, elbow, nipple and any other fitting near the fence and then to be extended to animal trough outside the fence using flexible HDPE pipe | No. | 1
تركيب نقطة تجميع حوض حيوانات جديدة بسعة 1 م 3 باستخدام لوحة MS بسمك 3 مم ، ويشمل العمل تركيب أنبوب حامل 63 مم (2 بوصة) مع صمام وكوع وأي ملحقات أخرى بالقرب من السياج ثم يتم تمديدها إلى حوض الحيوانات خارج السياج باستخدام أنابيب HDPE المرنة بحجم 2 بوصة .
2.7 | supply material and cast plain concrete with mix of 1:3:6 for the base of animal trough and donkey cart collection point | M3 | 0.642
خرسانة عادية بإسمنت عادي تحت البردين بسماكة 10سم مع الدمك و رش الماء و الصب باستخدام اسمنت بوتلاندي عادي 250كجم/متر3
2.8 | supply material (brick, cement, PPR pipe with fittings and tap) and rehabilitate the tap stand in Health facility | Service | 1
توريد المواد (الطوب والأسمنت وأنابيب PPR مع الملحقات و الحنفيات) وإعادة تأهيل حامل الحنفية في المركز الصحي
2.9 | conduct outside/inside inspection and repair of water elevated tank for any holes, rust or any other damages, the work include also applying of water proof painting | Service | 1
إجراء فحص خارجي / داخلي وإصلاح خزان الماء المرتفع بحثًا عن أي ثقوب أو صدأ أو أي أضرار أخرى ، ويشمل العمل أيضًا تطبيق طلاء مقاوم للماء
Water Point
3 | Excavation works of drainage pit حفرة التصريف
3.1 | Excavate for drainage pit measuring 1m x 1m x 0.5m depth as shown in drawings, and according to the supervisor's instructions. | M3 | 2
اعمال الحفر لحفرة التصريف 1متر *1متر *0.5 متر عمق بحسب الرسومات وتعليمات المهندس المشرف.
3.2 | excaviton of deainge trench length of 8 meters minimum, width of 30 cm and depth of 15 cm to frain excessed water from tab stand | Ml | 10
حفر و عمل مجرى تصريف بطول 10 أمتار و عرض 30 سم و عمق 15 سم لتصريف المياه الفائضة من نقطة مياه الحنفيات الى حوض التصريف
Sub Total5
Grand Total | Grand Total
International Rescue Committee (IRC), Sudan Program
Project Name: Lifesaving Primary Healthcare and WASH Services in Underserved Areas of Sudan
Funded by (BHA).
Intervention: Rehabilitation of Water Yard in Al Garri in Wd elmahi Locality, Blue Nile State