## Sheet1
Bill of Quantaies
Supply Materials and construction of two (2) Solar Pumping Systems at Al-Enqaz and Al-Andalous Boreholes in Wad Madani - Al Gezira State
No. | Description | Unit | Qty | # of Sites | Unit Cost SDG | Total Amount SDG
1 | Supply and fix crystalline solar panels1 Solar power pumping systems to drive (7.5 KW)/ 3 phase /380~415 ACV/50Hz, outlet diameter of the pump 3 inches. Solar PV modules (Trina or Jinko or JA solar or Longi): Crystalline modules shall meet IEC 61215 (2005-04): '' Crystalline silicon terrestrial photovoltaic (PV) module - Design qualification and type approval , IEC 61730-1,2: 2004 Ed photovoltaic (PV) module safety qualification . PV modules have to meet the following requirements :- * The type of photovoltaic (PV) module should be mono or polycrystalline . * The tolerance of rated output of the PV modules offered may not larger than [-3%] . * Crystalline modules shall have a bypass diode . * Information on the performance of the chosen modules in respect of current voltage charactertics at STC shall be submitted to verify that the output of the modules will meet the requirements of each of the systems. * The real out put of panels array Voc must be ≥ 730 V which is resd by the inverter (the pump drive) or the AVO meter and the Imp of panels array string must be ≥ 8.6 Or Voc must be ≥ 630 V which is read by the inverter (the pump drive) or the AVO meter and the Imp of panels array string must be ≥ 17 A * Labeling :Each module must be labeled indicating at a minimum : Manufacturer . Module number , serial number , maximum power point watt rating (Wp tolerance ), maximum power point current , maximum power point voltage , open circuit voltage and short circuit current of each module . * The module framing should be such that it permits secure connection to the mounting structure , prevents edge damage and has the longevity to with stand environmental factors for the duration of the module warranty period . * All PV modules within an array shall be of the same type and hence interchangeable . Module warranty :25 years : the PV modules must be warranted to retain at least 80% of its nominal rated output measured at STC for at least 20 years . * The panels must be attached to the support structure by means of screws into the slot in the panels which is designed for them . | Watt | 10900 | 2
2 | Supply and fix module Support Structure: * for solar array system in item (1) above , 15'' tilt angle (15 degrees to the horizontal facing the equator (south direction) for ground installation , must be made of corrosion resistant and strong material that assures stable and secure attachment , with stand high wind speed of (200 kw/hour) , the modules must be no shading from near by trees or buildings during the day and the legs of support structure must be anchored in concrete (made with 1:2:4 cement concrete ) deep in ground (at least 40cm x 40cm x 50cm) and 10 cm above ground . The legs and mounting structure must be sufficiently rigid to prevent twisting in the wind or if large birds on the array . The panels must be attached to the support structure by means of screws into the slot in the panels which is designed for them. The design of the support structure should be accept the installation as one or two unit. As per attached drawings. | Set | 1 | 2
3 | Supply and fix Power control unit (VFD) Inverter and other accessories (7.5 kw): The DC circuit breakers voltage must be ≥1000 v The Inverter must be :- * The input DC V : 750~ 900 V/output AC V : 3 phases 380 ~ 415 V , 50 Hz * have VFD/Smooth start technology * Inbuilt MPPT+VFD (Variable Frequency Drive ) to improve AC pump's efficiency and protect AC pump . * Pump protection when over –voltage and over – load , under – voltage , over current , surge , over – temperature , short circuit protection . * LED graphic display for pump / solar panel status and setting . With keys for easy operation . * Dry running protection by programming and sensor and self – restart function . * Waterproof and dustproof level up to IP20 . * Reliable for terrible environment , operate temperature -20 C ~ +60 C * the Control unit Box must be tied to support structure with two legs anchored in concrete (made with 1:2:4 cement concrete ) deep in the ground (at least 30 cm x 30 cm x 30 cm). | Set | 1 | 2
4 | Supply and fix wiring AC and DC flexible Saudi cables: For DC section : deferent color between solar arrays to junction box ≥ 6 mm2 , from junction box to power control unit (PCU) ≥ 10 mm2 . ( 2 core deferent color ) approximate length (90 m – 2 core 6 mm2 and 65 m – 2 core 10 mm2 The cable terminals to the array panels string terminals (positive and negative ) must be connect by MC4 connecter . * All cables joint must be coverage by waterproof cable joint kits . The cables should be insulated with especial grade PVC compound formulated for outdoor use any extension between the Support Structure units and to the electrical rooms must be buried in the ground 30 cm deep . | m | 30 | 2
5 | * Supply and fix control unit Box : GRP/FRP/ Power Coated Aluminum box to protect control unit with good ventilation and lock . Full protection of dust , water and vermin proof arrangement . | Pcs | 1 | 2
6 | * Supply and fix changeover switch 100 A / 4 Pole (German or Indian ) | Pcs | 1 | 3
7 | * Supply and fix Junction box: Shall be full dust , water and vermin proof arrangement placing of the junction accessories inside the PCU box is acceptable . | Set | 1 | 2
8 | Supply and fix earthling system, and lightning protection. | Set | 1 | 2
9 | Supply and install system Fencing around the solar modules circumference: Excavation of the pols foundation 40cm X 40cm X 60cm, fence dimensions 18m X 12m using Angle bars 3x3 inch and 5mm thickness, fabricate and fixing of (V) shape on top of the pols with the total length 50cm each using Angle bars 2X2 inch, painting of all pols 3 layers, fixing the pols at distance 2.5m c/c using cement concrete ratio 1:2:4, welding of reinforcement bars 16mm 5 layers to reinforce the fence, fixing of chain-link Ø 4mm @ 5x5cm c/c. fixing the riser wire Ø50cm on top of the fence as per attached drawings. | m | 30 | 2
10 | Supply and install door: 3m X 1.8m two sleeves using heavy steel pipes 8X4 cm for the frame and in the middle, fixing of vertical pipes 5X2.5cm at 15cm c/c, fix steel shape 1mm thickness 120cm X 70cm two pieces on the middle of the door, fixing of the door sleeves on two pols (ɪ) section 12x12mm (5mm thickness) 2.5m length with 8 hinges made of GI pipes 1" and ¾" and fixing of 3 lock traps with two padlocks in and outside, painting of the door three layers and print a logo, as per attached drawings. | Set | 1 | 2
11 | Supply and Install signpost 120cm X 240 cm fabricated from steel sheet 1mm thickness and Angle bars 3X3 inch, fix the signpost with cement mortar 1:2:4 in foundation 49X49X60cm and rise 1.5m above ground level. | Pcs | 1 | 2
Total
Supplier Information |  |  |  |  | Vender Stamp
Name
Tel
Title
Signature
Date