## Shinteshrab
Solar panel estimation for BLNS Shinteshrab BH
| Current Benf no. |  |  | 6500 individuals | [6 empty] | population growth | PN | = | P0 | x | (1+r/100)N
| Current demand domestic |  |  | 97500 | lits/day | 97.5m3/day | [6 empty] | = | 6500 | x | (1+2.4/100)20
|  |  |  | 10833.3333 | lits/hr | [7 empty] | = | 6500 | x | (1.024)20
| Current demand institutional |  |  | 1000 | lits/day | 1m3/day | [7 empty] | 6500 | x | 1.6069
| Total current demand |  |  |  |  | 99m3/day | ~ | 100m3/day |  |  |  |  | = | 10445
| Forecasted demand domestic |  |  |  | 156675 | lits/day
| Forecasted institutional demand |  |  |  | 1000 | lits/day
|  | Total forecasted demand |  |  | 157675 | lits/day | 158m3/day | - with both generator and solar as energy sources
[6 empty] | Inorder to optimize- |  | Assuming 2hrs of generator operation then solar array has to be estimated for 7hrs of running
| Design discharge for solar |  |  | 17.5556 | m3/hr
|  |  |  | 4.8765 | lits/sec
| Solar pump design discharge needed as per current benf |  |  |  |  | 5lit/sec
Actual Borehole discharge estimated |  |  |  | 30 | m3/hr | 270 | m3/day
|  |  |  | 8.3333 | lits/sec
Actual 7.5kw AC pump existing in the borehole discharge |  |  |  |  | 8lits/sec
| PSH | = | 5.9kwh/m2/day
option 1- Solar array determination
power of pump(W) x hours pump running(h)= Solar array power (W) xPSH(h)x PR
|  | Solar array power (W) | = | 14830.5085 | W
|  | considering 250W panels |  | 59.322 | ~ | 60 | panels
|  | considering safety for wastage and losses |  |  |  | 62 | panels
option three - Solar array determination
|  | Hydraulic Energy required |  | EH= QHÞg/η
|  | or | EH(in KWH/day) | = | daily water volume (m3/day)x TDH x1000*9.81 |  |  |  | = | daily water volume (m3/day)x TDH x2.725
3.6*1000
[9 empty] | = | 30138.5
|  |  | Daily energy demand | = | Eh/Pump performance |  |  | = | 40184.6667
|  | Solar array power required (in kwp) |  | = | Daily energy demand |  |  | = | 40184.6667 | = | 11351.6008
[5 empty] | PSHx Performance ratio |  |  |  | 3.54
|  | considering 250w panels |  | = | 45.4064
|  |  |  | = | 46 | Panels
|  |  |  | ~ | 48 | Panels considering various losses and wastage

## ND BH15
Solar panel estimation for North Darfur BH 15
|  | Current Beneficiary no. |  | 2400 individuals | [6 empty] | population growth |  | PN | = | P0 | x | (1+r/100)N
|  | Demand domestic |  | 36000 | lits/day | 36m3/day | [7 empty] | = | 2400 | x | (1+2.4/100)20
|  |  |  | 4000 | lits/hr | [8 empty] | = | 2400 | x | (1.024)20
|  | Demand institutional |  | 1000 | lits/day | 1m3/day | [8 empty] | 2400 | x | 1.6069
|  | Total Current demand |  |  |  | 37m3/day | [7 empty] | = | 3857
|  | Forecasted domestic demand |  |  | 57855 | lits/day
|  | Forecasted institutional demand |  |  | 1000 | lits/day
|  | Total forecasted demand |  |  | 58855 | lits/day | 59m3/day | - with both generator and solar as energy source
[6 empty] | Inorder to optimize- |  | Assuming 2hrs of generator operation then solar array has to be estimated for 7hrs of peak running
| Design discharge for solar |  |  | 6.5556 | m3/hr
|  |  |  | 1.821 | lits/sec
| Solar pump design discharge needed as per current benf |  |  |  |  | 2lit/sec
| Actual Borehole discharge estimated |  |  | 4.32 | m3/hr | 38.88 | m3/day
|  |  |  | 1.2 | lits/sec
[5 empty] | 2 | lits/sec
Actual 2.2kw AC pump existing in the borehole discharge |  |  |  |  | 1.2lits/sec
| PSH | = | 6.3kwh/m2/day
option 1 - Solar array determination
power of pump(W) x hours pump running(h)= Solar array power (W) xPSH(h)x PR
|  | Solar array power (W) | = | 4074.0741 | W
|  | considering 250W panels |  | 16.2963 | ~ | 17 | panels
|  | considering safety for wastage and losses |  |  |  | 19 | panels
option 2 - Solar array determination
|  | Hydraulic Energy required |  | EH= QHÞg/η
|  | or | EH(in KWH/day) | = | daily water volume (m3/day)x TDH x1000*9.81 |  |  |  | = | daily water volume (m3/day)x TDH x2.725
3.6*1000
[9 empty] | = | 8502 |  | - solar array estimated with existing BH discharge
|  |  | Daily energy demand | = | Eh/Pump performance |  |  | = | 11336
|  | Solar array power required (in kwp) |  | = | Daily energy demand |  |  | = | 11336 | = | 2998.9418
[5 empty] | PSHx Performance ratio |  |  |  | 3.78
|  | considering 250w panels |  | = | 11.9958
|  |  |  | = | 12 | Panels
|  |  |  | ~ | 14 | Panels considering various losses and wastage