|  |  |  |
| --- | --- | --- |
| # | Question | Answer  |
| 1 | Appendix 11. Habila PHCsinstallation in Fayo PHC:a. What are the needed working hours for the system?b. How many watts are the lamps? c. The capacity of the inverter 850w isn't available with 48v; it can only be found with 12v or 24v. d. The cable is 4mm multiplied by how much?  | a. 6 hours max.b. 40 wattc. if the company intended to supply  Hybrid Solar Power Inverter with built-in charge controller then it should be 24v , but if the company will supply tow sperate devices ( invertor and charger controller) then the capacity of the charge controller should be 48v , 30A.d. its 4mm \* 30 meter length as detailed in the BoQ |
| 2 | Appendix 21.Abokarshola localityinstallation in Alrokaba. what is the horsepower of the water pump?b. and the watts of the lamp?  | a. it is 0.5 HP.b. 40 Watts each. |
| 3 |  |  |
| 4 |  |  |