## Slide 1
Location: Babikri/Doka/TUN
Lat: -……….
Long: .............
Alt: ,.......
Nominal depth: 70m
SWL: 10mbgl
Steel Surface Casing: 3m
Surface Casing grouted
4’’ PVC casing cement sealed to 5 mbgl
4’’ PVC blank casing
4’’ PVC slotted casing: 1mm slots
Backfill above bentonite seal
Bentonite seal above gravel pack
Borehole annulus gravel packed: 3 to 5mm graded, washed, inert quartz gravel.
4’’ sump with end cap
Note: The drilled exploration boreholes will be completed with casing, gravel pack, bentonite seal and surface sanitary seal (depending on tested yield). Those with low yield will have only PVC casing and an end cap installed. Max depth will be 70m but could be lower (even 30m) depending on yield of aquifer(s) penetrated.