بسم الله الرحمن الرحيم

بلان العالمية السودان – مكتب دارفور

التاريخ /18/08/2020

إعلان مناقصة عامة رقم (2) للعام 2020 م

تعلن بلان العالمية السودان – مكتب دارفور عن طرح مناقصة لترقية وترفيع مضخة يدوية الى محطة مياه صغيرة بقرية كنجار تاني محلية طويلة ولاية شمال دارفور – الفاشر.

شروط عامة:

- تقدم المناقصة وفقا لمواصفات وجداول الكميات المعدّة في كتيب المناقصة.

- ارفاق صورة من الرخصة التجارية سارية المفعول.

- خلو طرف من الضرائب (او اعفاء) او شهادة ملف الضرائب سارية المفعول.

- إرفاق خلو طرف من الزكاة.

- أن يكون لدي الجهة المقدمة مهندس للإشراف على العمل.

- شهادة قدرة مالية.

- شهادات الخبرة او مرجع من الجهات التي تم التعامل معها في هذا المجال.

- اي مستندات يمكن ان تساعد في المنافسة.

- يحق للجنة فرز المناقصة حسب المواصفات المرفقة.

- اللجنة لا تتقيد باعلى او أدني الاسعار.

- الالتزام بمواعيد تسليم استمارة المناقصة.

- الكشط اوالتعديل غير مقبول.

- يجب أن تدرج الأسعار في المبلغ النهائي للعروض وفقا لكراسة المناقصة.

- يجب على المتقدمين تحديد الفترة الزمنية لإكمال العمل وتسليم المحطة.

- يتم تسليم الموقع حسب الفترة الزمنية المحددة تحت إشراف لجنة من هيئة المياه بالولاية والمنظمة والمجتمع المستفيد والجهة المنفذة.

فالرجاء إستلام كراسة المناقصة مختومة من إستقبال المنظمة والتكرم بتقديمها ووضعها بصندوق المناقصات بإسـتقبال المنظمة التي تقع شمال المستشفى السعودي وذلك في الفترة من 18/08/2020 م وحتى 31/08/2020م اثناء ساعات العمل الرسمية من 8:00 ص - 4:00 م. وللاستفسار يرجى الاتصال بالرقم: 0900934149

سيتم فتح مظاريف المناقصة بحضور مقدمي المناقصات يوم الاربعاء الموافق 02/09/2020 م الساعة 12:00 نهارا بمكتب المنظمة شمال المستشفى السعودي بالفاشر.

ملحوظة:

- التقديم بصور من الشهادات والمستندات المذكورة انفا وليس الاصل.

| رقم | الصنف | الوحدة | الكمية | سعر الوحدة | الجملة | تاريخ تسليم محطة المياه |
| --- | --- | --- | --- | --- | --- | --- |
|  | ترقية وترفيع مضخة يدوية الى محطة مياه صغيرة محلية طويلة (قرية كنجارات) | ترقية وترفيع مضخة يدوية الى محطة مياه صغيرة | 1 |  |  |  |
| الجملة |  |  |  |  |  |  |

إسم المقاول /:.....................................         التوقيع/............................

الختم:................................................

رقم الهاتف:........................................

التاريخ:.............................................

Invitation of public Tender No: (2) 2020 Al fasher:

Plan International Sudan - Darfur office announces a tender for upgrading of hand pump to a small water Yard in Tawila locality (Konjarat A&B) Villages.

General Terms:

• The tender shall be submitted according to the specifications and tables of quantities prepared in the tender booklet.
• Attach a copy of a valid commercial license.
• Free from tax (or exemption) or valid tax file certificate.
Attachment valid documentation of Zakat.
• The provider must have an engineer to supervise the work.
• Financial ability certificate.
• Certificates of experience or a reference from the authorities that have been dealt with in this field.
Any documents that could help with the competition.
• The committee has the right to sort the tender according to the attached specifications.
• The committee does not adhere to the highest or lowest prices.
• Commitment to deadlines for submitting the tender booklet.
• Abrasion or modification is not acceptable in booklet.
• The prices must be included in the final amount of the offers according to the tender booklet.
• Applicants must specify the time period for the delivery Water yard .
• The work deliverey according to the specified time period, under the supervision of a committee from the water administration, the organization, the beneficiary community and the implementing agency.
Please receive the tender booklet  from the organization’s reception and kindly submit it to the tender box at the reception of the organization located north of the Saudi Hospital, during the period from 18/08/2020 until 31/08/2020 during official working hours from 8:00 a.m. - 4:00 p.m. For inquiries, please call: 0900934149
Tender envelopes will be opened in the presence of the bidders on Wednesday, 02/09//2020 at 11:00 am at the organization's office north the Saudi Hospital in Al fasher.

Note: Submitting only copies certificate, not original.

| Delivery date | Total amount | Unit price | Quantity | Unit | Discription | No: |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | 1 | Hand pump | Upgarding of hand pump to water yard | 1 |

------------------------------ Name of contractor

Signture-----------------------------------------------

Stamp-----------------------------------------------

Cell phone-----------------------------------------

Date------------------------------------------------

BOQ of upgrading of Hand Pump to Mini Water Yard (Tawila – Kungara A&B)

| No | Items | Unit | Quantity | Unit Prices SDG | Total price SDG |
| --- | --- | --- | --- | --- | --- |
| 1 | Procurement and installation of Submersible pump diameter of outlet 1.25 inches, H=65m, Q= 5 m3/ Hours made in Italy with accessories cable raising main 11/4 inches completed with socket = 120 meter (Please the Submersible must work both system, Generator system and Solar) | job | 1 |  |  |
| 2 | Raising main (Indian mark 11) for installation of bore holes (steel galvanized pipe 3 meter) | Pcs | 15 |  |  |
| 3 | Supply and installation Diesel Generator 18HP, Three Phase cylinder water cooling made in Poland with Dynamo cooper 10kwh made in China. construction water storage, building bricks, cement and well plastering size (2*2*2m) velum 5Berol water for cooling. | Sum | 1 |  |  |
| 4 | Supply materials and construction Generator house, 4m X 4m, high 3.2m, by sheet iron wall, foundation 50 cm with red bricks plastered painted, corrugated Iron sheet for Roof and wall surrounding, with properly constructed lockable gate and two window and one Door (1.5m*2m). use steel box 8*4cm with vertical frame legs by steel angle 2.5inch thickness 3mm. | Sum | 1 |  |  |
| 5 | Construction of water storage steel elevated tank, with capacity of 15 cubic meter, 6 meters elevated, and detail as SWC standard. Foundation, structure of steel legs. | job | 1 |  |  |
| 6 | Construction of water distribution point (10 valve), details as SWC standard. Including Taps 1 inch, pipe line 3 inch along from the tank, construction table By Bricks and plastering. (Two water points) | job | 2 |  |  |
| 7 | Fencing of the water distribution 20m× 20m× 2m including for water points (public fountain, motor house, tank area, solar area 10*10 m) and separation animal from human area Wire mesh square 7*7 cm thickness 4mm, (use pipe steel angle 2-inch-long 2.4 m, thickness 3mm, distance 2each pipe) with cross fixed connection angle 1.5 inch. Painting by white /black colour. | ML | 100 |  |  |
| 8 | Procurement and installation (made by steel higher quality) of animal trough, capacity one cubic meter for each as SWC standard. | Pcs | 2 |  |  |
| 9 | Connection form well to elevated tank and tap stand 100-meter-long (steel galvanized pipe 3 meter (2 and 3 inch)) with all support accessories. Please use from Tank to distribution point by 3inch. | ML | 100 |  |  |
| 10 | Consulting engineer and Lobar cost | Process | 1 |  |  |
| 11 | Transportation of materials and equipment and engineers to the field cost of | Trips | 1 |  |  |
| Total cost |  |  |  |  |  |

Specifications and Orientations.

This is part of Bill of quantity as specifications: -

The specification of water Tower

- Steel legs comer (IPN200).

- The main foundation (IPN200).

- The water tower base (IPN200).

- The connection steel by steel angle 3 Inch thickness 3mm high quality.

- The second connection steel by steel angle 2.5 Inch thickness 3mm high quality.

- Painting work in very good finalization (properly white and black colour)

- Concoction pain well fixed from concrete foundation to join steel legs.

The specification of concrete foundation base

- Foundation of 4Shourt Colum’s (1*1 depth 1.5m) excavation work.

- Plain concrete 10cm with steel base (steel 12mm c/c 10cm)

- Fixed the steel frame Colum (60*60cm) use steel 16mm-8 pieces with surrounding concoction c/c(20cm) 9mm (1.5m high*60*60) according the others natural land or level.

- Foundation Great beam (35*30) cm, by 12m 8picess, use steel 9mm as c/ 20cm.

- Plaint concrete for floor work.

The specification of fencing work

- Foundation digging for fixing the steel pile (50*40depth) cm.by concrete.

- The pipe must be by steel angle 2inch high quality thickness 3mm. distance 1.5 m with top join by steel box 6*3cm high TH.1mm.

- The steel wire mesh must be very clear as specification (square 7*7cm, high 2m, and thickness 4mm) with all accessories.

- Panting work in very good finalization (properly white and black colour).