## AL Regiala Borehole drilling
اسم الشركة Company name
General manager مدير الشركة
Address/Mobile العنوان / موبايل
Delivery period فترة التسليم
Validity of offer صلاحية العرض
Deadline 25/10/2022 اخر يوم للتقديم
BoQs of provide materials and Drilling of deep borehole in Regaila Village Yassin locality
LOCATION: Regaila village of yassin Locality
No | Description | Unit | Unit price | Quantity | Total Cost
1 | Mobilization and demobilization of machines and equipment :
1.1 | Mobilization and Demoblization of crew, drilling rig, drilling tools, Materials and Technical and Non-technical staff and all the required materials for this contract | job |  | 1
1.2 | Site cleaning, before and remove of the waste/rubbish materials, Backfilling the pits after construction. | job |  | 1
1.3 | Construction of camp facility and setup of the rig. | job |  | 1
2 | Drilling of the borehole :
2.1 | Drilling in all types of formation using rotary or DTH system with bit diameter of 14". | M |  | 130
2.2 | Sample taking and Lithological logging every 2 meters | Sample |  | 65
2.3 | Supply and install API/ASTM plain casing of 8 5/8" diameter size and wall thickness of 5.2mm as minimum, threaded on both sides. (Note: If threaded is not provided, the welding cost with reinforcement connections price should be included together with supply & installation cost) | M |  | 100
2.4 | Supply and install screen casing pipes of continuous V-shape slot Johnson screen with diameter 8 5/8", 12 bar and slot 0.02 mm, made of non-clogging wrapped wire welded over longitudinal rod base and manufactured from galvanized stainless steel and joints fitted with male and female threaded ends. | M |  | 30
2.5 | Conduct data logger for the borehole. | job |  | 1
2.6 | Supply materials and carryout gravel packing using selected river gravel size 4-6mm ( rounded or sub rounded ) and standard (supplied from Al Jaily Area). | M3 |  | 12
2.8 | Borehole sealing with mass concrete to a depth of 6 meter, and construct well head ( 1.5*1.5*0.5 meter ) C:25. | M3 |  | 2
2.9 | Supply and install of wall cap | cap |  | 1
3 | Well cleaning and development using air compressor. | Hrs. |  | 12
3.1 | Well cleaning ( backwashing ) in & Outside the casing | Job |  | 1
3.2 | Conduct air compressor for the borehole till the cleaning of the bore hole | job |  | 1
4 | Borehole and water quality Testing
4.1 | provide equipment and Conduct continuous pumping and drawdown test for as minimum 12 Hrs. | Hrs. |  | 12
4.2 | Conduct Water quality test (chemical, physical and bacteriological) in for parameters (according to SSMO water quality test list), in certified lablotary and provide detailed water quality report, approved and stamped by the lab. | Test |  | 1
4.3 | Conduct Data analysis and provide compiled drilling and pump test reports in two hard copies using the standard SWC ( State water corporation) and, 1 electronic copy (in Flash Drive) with chart and pictures. | Report |  | 1
5 | Borehole installation :
5.1 | Supply and install submersible pump + Motor 7.5 KW , with following specification : Pumped liquid: Water, temperature range: -15 .to . 40 °C Technical: Pump speed on which pump data are based: 2900 rpm. Actual calculated flow: 28 m³/h, Rated flow:14 m³/h Resulting head of the pump:120.4 m, Rated head:117.9 m Return valve: YES, Materials: all Impeller, Motor, stainless steel Motor diameter: 4 inch Minimum borehole diameter: 105 mm Rated power - P2: 7.5 kW Power (P2) required by pump: 7.5 kW Mains frequency: 50 Hz Rated voltage: 3 x 380-400-415 V Rated current: 18.4-18.8-19.6 A Starting current: 490-530-550 % Cos phi - power factor: 0.83-0.78-0.72 Rated speed: 2830-2850-2870 rpm Start. method: direct-on-line | SET |  | 1
5.2 | Supply and Install of new Standard GI ASTM raising main pipe, 2 inch in diameter, 3 meter long, class C, threaded (Hard thread) in both sites and with socket attached. | PCE |  | 40
5.3 | Supply and install of standard control panel for the 7.5 KW submersible pump motor (Grundfos). | PCE |  | 1
5.4 | Supply and install clamp made of heavy steel 7mm thickness, with bolt 16 mm. | PCE |  | 1
5.5 | Supply and installation of electric Cable 10 mm, flat, three phase, exported (manufactured in Saudi Arabian is preferred). | meter |  | 150
5.6 | Supply and install of fine finish, Ruggedness, Highly durable non-returning valve 2inch made of iron (Zahar) with pair of flange. | PCE |  | 1
| Grand Total |  | 0
| Sign & stamp |  |  |  | Date
| الختم و التوقيع |  |  |  | التاريخ