- Solarization                                                         Standard Bill of Quantity for Provision of Solar system in Women Center – Gubysh Area – PRF # 0171 -NS23007-723

The specified job is all provisional, including the provision of materials and workmanship, and all other requirements to implement the job perfectly. The cost of this item should be included /embedded in the other items. Below is the BOQ:

| 1:00 | SOLARIZATION WORKS |  |  | Unit Price | Total Cost SDG |
| --- | --- | --- | --- | --- | --- |
| 1.1 | Solar Panels: Supply & installation of robust 330-watt peak 24 volts,8,8 Amp, solar panels must have one of these ISO, CE RoHS, UL, IEC, and TUV Certificates. Each PV module deployed must identification tag which should be able to withstand harsh environmental conditions and consist of the following information: * Name of the manufacturer of the Solar panels. (PV modules) * Month and year of manufacture for each solar Panel. * Panel (Module) Wattage, Imax, Vmax, FF …etc. * Unique serial number of the Panels (PV modules). | Pcs | 14 |  |  |
| 1.2 | Batteries: Supply Led Acid (GEL) deep cycle batteries,200 Ah 12- Volt. & Batteries must have one of these accreditation certificates such as ISO, CE, RoHS, IEC…etc. Or has passed the UNDP lab test (Sudan). They must be manufactured at most in the latest (06) six months. | Pcs | 16 |  |  |
| 1.3 | Inverter: Supply & install with capacity power 5000 VA, Volt 48 V rated, The Inverter must meet one of these, ISO, CE, RoHS, IEC Certificates. The Inverter must meet below: *Charge controller MPPT build-in. * Output details: Pure sine wave, 230 V, Single phase, 50Hz. * Efficiency: >95%. * Overloading features: 150 % for 1 min (Surge Power). * Cooling: Forced air-cooling with temperature-controlled automatic cooler fan. * Operating temperature :0 to 50 deg C. * Can work efficiently under condition relative humidity: 95% * Enclosure protection IP 54. * Protections must be provided: * Input voltage protection: (Undervoltage, over-voltage) * Output voltage protection: (Undervoltage, overvoltage). * DC reverse polarity. | Pcs | 1 |  |  |
| 1.4 | Modules Mounting Support Structure (MMSS) (to hold 14 (Pcs) of solar panels)): Supply, Fabricated, construction, and installation of the Bolted support structure to hold modules, the support structure should be made from hot dip galvanized steel or heavy pipe & angles with precoated anti-rust as base paint & colour paint, and the Support structure withstands wind speed (40 m/sec) if the support structure it’s a ground-mounted, the base of concrete (30*30*50) cm. | Each | 1 |  |  |
| 1.5 | Batteries Racks To hold (16) Pcs of batteries: The rack should be from Aluminium or heavy iron angles & pipe with precoated anti-rust as base painting + colour painting. | Each | 1 |  |  |
| 1.6 | Dc Cables 16 mm (rolls): Supply Dc cables (100 yards) single core with red colour & black colour the cables must be hosing with conduit or plastic (PVC) pipe for protection, cables shall meet the requirements of one of these certifications ISO, RoHS, IEC, and TUV. | rolls | 2 |  |  |
| 1.7 | Junction boxes for Solar Panels with Dc Fuses: The Junction box must be manufactured from fiberglass reinforced plastic (FRP)/ thermos plastic with IP65 protection, & shall be waterproof, and dustproof. The terminals should be connected to copper bus bar arrangement of proper sizes to connect cables from solar modules arrays & Inverter. The Junction box must have protection devices below: DC -Fuses (16) Pcs (15 Amp 500 Volt) with Busbars embedded with cable glands, & conduit. | Each | 1 |  |  |
| 1.8 | Junction boxes for batteries with DC Circuit breakers: The Junction box must be manufactured from fiberglass reinforced plastic (FRP)/ thermos plastic with IP65 protection, & shall be waterproof, and dustproof. The terminals should be connected to copper bus bar arrangement of proper sizes to connect cables between Batteries & Inverter. The Junction box must have protection devices below: DC Circuit Breakers (6) Pcs 500 Volt, 500 Amperes with Busbars embedded in addition to that cable glands, & conduit. | Each | 1 |  |  |
| 1.9 | Interconnection Cables: Dc cables 25 mm, ready-made jumpers. For interconnections batteries. | Each | 1 |  |  |
| 1.10 | Fencing: Providing & construct galvanized iron poles 2-inch Dim, height 2 m with concrete Base 30*30*40 cm with chain-link wire with a secure distance of 3.5 m for each direction (distance between fence & solar panels). | Work | 1 |  |  |
| 1.11 | Accessories: Nuts, clips, tapes cables clamps …etc. | Job | 1 |  |  |
| 1.12 | Lighting arrester& earthing: Has cable 16 mm, 20 Meters, Star, equipotential busbar, earthing rods, set of joint cable, set of screws to the joint module via support structure. | Set | 1 |  |  |
| 1.13 | Installation & testing & commission of solar system above. | Work | 1 |  |  |
| 1.14 | Total Cost in SDG |  |  |  |  |