## Solar System & Chain Link Fence
General information for RN borehole-Bajbouj
Requisition# 4042139
Borehole Solarization and Chain Link Fence in River Nile State
| WY name | Yield m3/h | Total Head /m | pump capacity/Kw
| Bajbouj & Alsalam Water Point | 22.5 | 100 | 12
Bill of Quantities & specifications for solar water pump system for Bajbouj&Alsalama Villages RN
Item | Specifications | Unit | Quantity | USD Unit Price | USD Total Price
1 | Water Solar System
Submersible pump system
1.1 | Supply & install and commission of solar powered submersible pump capable of Q= 22.5 m3/hr. and H=100 m according to the borehole data. Submersible pump system including controller with Data Module, motor and pump end (European in origin such as LORENTZ, Grundfos, Panelli, etc.) (Certification from NSF/ANSI 61 or another international standard from ISO, ASTM, IAPMO, etc.) Performing at not less than 70% efficiency. Pump impellers made of stainless steel; electric motor winding suitable for electric supply, and water temperature of 35 C, body size of pump bowel assembly + motor should have factory built-in non-return valve and strainer. With heavy gauge riser. (setting depths based on the wells specifications attached to this bid document and design report) | PCS | 1
Solar PV Modules
1.1 | Solar PV modules (recommended capacity on single module 550 Wp) according to the following specifications: Mono or Poly Crystalline Silicon Solar cells should be used in the solar module that are used for Solar Water Pumping application. - Modules supplied with the Solar Water Pumping systems shall have certificate from recognized institute. - Modules must qualify to IEC 61730 Part I and II for safety qualification testing. - Power temperature coefficient of PV modules shall be at most: - 0.043%/0C. - Each module must be labelled indicating at a minimum: Manufacturer, Model Number, Serial Number, Maximum Power Point Watt Rating (Wp tolerance), Maximum Power Point Current, Maximum Power Point Voltage, Open Circuit Voltage and Short Circuit Current; and temperature coefficients. - All PV modules used in the array offered for one project must be of same type, same model, same power rating and same manufacturer - The PV modules must be warranted to retain at least 90 % of its rated wattage measured at STC for 10 years and 80% of the rated wattage at 20 years. | Module | 30
1.2 | Solar pump control unit or drive inverter according to information given in above table with minimum power of 15 KW. It should be installed within the modules support structure and shall convert the direct current, DC, from the solar PV array into alternating current,AC, for driving deep well water pump AC motor water pump. The inverter input shall be the solar panel DC power supply, and with built-in MPPT control system to maximize the output power of the PV array. It should be suitable for use in remote and dry areas and shall match the power from the PV array to the demand of the pump motor allowing the pump to start even during weak sunlight periods. (German or equivalent high quality inverter) | Controller | 1
Solar Water Pump controller or drive inverter
1.3 | Support Structure for solar PV array system in item (3) above, 20˚ tilt angle and to withstand high wind speed of (40m/s), on concrete base (50*50*70 cm) with the front legs 2 meters above ground level. According to the following technical specifications: - The Solar PV modules should be ground mounted on metallic structures of adequate strength and design that can withstand weight of the modules and high wind velocities up to 150 km/hr. - The modules should be ground-mounted with silver painting or hot dip galvanized. - The array mounting structure will hold the photovoltaic modules. The modules must be mounted on a support structure made of corrosion resistant material that assures stable and secure attachment. - The structure must be mounted such that the modules are at a tilt angle of 20 degrees to the horizontal facing the equator. - The support structure for solar array system shall be on concrete base with the front legs 2.0 meters above ground level. - There should be no shading from nearby trees or buildings in the solar module. - All nuts and bolts should be made of very good quality and should be corrosion resistant. - The structure should be designed to allow easy replacement of any module. - To minimize theft risk, Module’s fixation on the support structure must be of anti-theft type. The minimum requirement for support structure is as follows: -Iron angle of 2 ½× 2½ inch, 5 mm thickness, for main structure, and square pipe of 8 × 4×1mm with 1½ inch iron angle wild on it for connections, and support legs should be made from 12 cm I section iron channel with 4 mm thickness, the front legs should be 2 m high from the ground. - Foundation of pump structure to be of size 50 × 50 × 70 cm | SET | 1
Controler to Motor Pump Cable
1.4 | Provision and installation Motor cable 10 m 6 mm² 3-phase cable for power and 1-phase cable for ground | M | 120
Wiring Works
1.5 | Wiring between solar array junction box and pump controller minimum 2 core x 10 mm² (black & red) and Connecting all accessories, solar cell together and joining with solar controller | Job | 1
Pump Operating Switch (AC Power Pack)
1.6 | A manual transfer switch ( change over swich) to operate the pump from a generator with two voltage disconnected Switches, Ensure switch rating is compatible with ≥15 kW pump load. | SET | 1
PV Disconnect Switch
1.7 | PV Disconnect Switch with specifications matching the design parameters of PV system (No. of string, Max. Volatage and current) | SET | 1
Steel box for the Controller
1.8 | Steel box for the controller or drive inverter and two switches with good ventilation and lock (IP65), Ensure size fits a ≥15 kW inverter | Pcs | 1
Total (USD)
| BOQ River Nile Borehole Solarization, Aldamar locality, Alsalam & Bajbouj | Unit | Quantity | USD Unit Price | USD Total Price
3 | Chain-link Fence 20x20ml for Solar System
Pricing shall include all necessary fittings and accessories for fence fixing. All materials should be approved by engineer prior to construction in site. All steel sections shall be painted. Colors must be according to Engineer instructions.
3.1 | Excavate trench as holes/pits for 62 poles foundation with dimension 0.3x0.3x0.5m (length, width and depth) and remove the soil away from the site | m³ | 2.79
3.2 | Provide & cast of iron angle poles 3 inch" thickness 5mm , 2.5ml, 0.5ml to be casted using plain concrete cement ratio 1:3:6 | Pcs | 62
3.4 | provide and install iron bar 2.8m length angle bar 2.5 inch 5mm thickness ,0.5m to be casted using plane concrete mix 1:3:6 as diaginol supporter and distributor every 5 ml | Pcs | 16
| Provide & construct chain-link 2m height for fence 80ml,wilded to tension steel bar 10mm for three round | ml | 78.5
4.8 | Provide and fix security razer wire size 50cm diameter over the metallic frame. using Angle bars 2 x2 inch and 3mm thickness, fabricate and fixing of (V) shape on top of the pols with the total length 50cm each using Angle and 2 bar 12mm Parallel and the price include weilding and bonding and painting | ml | 80
4.9 | provide and fix steel gate (1.5x2 m) made of iron bar mesh (13 mm) steel angle 2x2 inch 3mm thickness, with lock (Big size) | No. | 1
4.13 | Provide materials and fabricate with paint WVI signboard size 120x150cm by using 4x8 square pipe and heavy steel sheet, signboard should include Solarization details . | pcs | 1
Total (USD)