## Sheet1 (hidden)
BOQs for Brackish Water RO Plant (50 m³/day) in Port Sudan
Item No. | Description with Notes | Unit | Qty | Unit Rate (USD) | Total (USD)
1 | Civil Works
1.1 | Site clearance, levelling, and compaction (remove vegetation, debris, and level to ±10 mm). | m² | 150 | 10 | 1500
1.2 | Reinforced concrete slab (200 mm thick, C25/30 concrete, with steel mesh BRC A142), for RO unit and ancillary rooms. | m² | 50 | 30 | 1500
1.3 | Perimeter fencing (chain-link mesh 2.5 m height, galvanized, with concrete posts every 2.5 m, foundation 300 mm wide × 500 mm deep). | m | 60 | 10 | 600
1.4 | Guard room (3 × 3 m) – reinforced concrete walls, plastered inside/outside, steel door, 1 window. | lump sum | 1 | 2000 | 2000
1.5 | Separate room for solar system and batteries (4 × 3 m), ventilation grills, steel security door. | lump sum | 1 | 3500 | 3500
1.6 | RO plant room (6 × 4 m) with ventilation fans, waterproof coating, and service trench. | lump sum | 1 | 4500 | 4500
2 | Mechanical & Process Equipment
2.1 | Raw Water Feed Pump – Vertical Multistage SS 316 Pump – Capacity 5–6 m³/h @ 6–8 bar, motor 3-phase, IP55, TEFC; includes suction strainer, flexible coupling, and isolation valves. Complies with ISO 5199 / API 610 for pump design. Includes installation, alignment, and testing. | No. | 1 | 1500 | 1500
2.2 | High-Pressure Pump for RO – Horizontal multistage SS 316, capacity 2.0–2.5 m³/h @ 16–18 bar; motor 3-phase IP55, TEFC, with stainless baseplate and flexible coupling guard. Complies with API 610. | No. | 1 | 5600 | 5600
2.3 | Multimedia Filtration Unit – FRP pressure vessel, dia. 600 mm, height 1800 mm, max. pressure 10 bar; media: graded silica quartz + anthracite; manual multiport valve, sch.80 PVC piping; complies with AWWA B100. Includes media filling, testing, and flushing. | No. | 1 | 2500 | 2500
2.4 | Activated carbon filter – FRP vessel, 1.2 m dia × 1.8 m height, coconut shell carbon, iodine number > 1000 mg/g. NSF/ANSI 61 certified. Includes full carbon fill, backwash, and commissioning. | No. | 1 | 1800 | 1800
2.5 | Cartridge Filter Housing – SS 316, 5-round, 5-micron PP cartridges, rated 10 bar, quick-clamp closure, drain & vent ports; ASME BPVC compliant. Includes initial set of cartridges. | No. | 1 | 350 | 350
2.6 | RO membrane housing – FRP, 4" × 40" size, suitable for brackish water, 8 elements in series. | No. | 2 | 1200 | 2400
2.7 | RO membranes – Dow FilmTec BW30-4040 (or equivalent), salt rejection ≥ 99%, 8 pcs. | No. | 8 | 1300 | 10400
2.8 | Permeate storage tank – HDPE, 5 m³, food-grade, UV-protected, top manhole & vent filter. | No. | 1 | 2200 | 2200
2.9 | Chlorination dosing pump – diaphragm type, 0–5 L/h @ 5 bar, PVDF head, with 50 L chemical tank. | set | 1 | 1000 | 1000
2.1 | Antiscalant dosing pump – diaphragm type, 0–5 L/h @ 5 bar, PVDF head, with 50 L chemical tank. | set | 1 | 1000 | 1000
3 | Electrical & Solar Power System
3.1 | Solar photovoltaic panels – monocrystalline, 550 Wp, Tier 1, IEC 61215/61730 certified. | No. | 18 | 1800 | 32400
3.2 | MPPT solar charge controller – 150 V, 100 A, programmable, with LCD display. | No. | 1 | 800 | 800
3.3 | Lithium-ion battery bank – 30 kWh total capacity, ≥ 6000 cycles @ 80% DoD, rack-mounted. | set | 1 | 5000 | 5000
3.4 | Inverter – hybrid type, 11 kW continuous output, pure sine wave, with grid/backup generator input. | No. | 1 | 3500 | 3500
3.5 | Electrical wiring & accessories – XLPE copper cables, armored for outdoor runs, complete with conduit, cable trays, breakers. | lump sum | 1 | 2000 | 2000
4 | Plumbing & Piping Works
4.1 | Raw water pipeline – uPVC PN10, 2" dia, with unions, elbows, tees, and valves. | m | 50 | 10 | 500
4.2 | Permeate line – uPVC PN10, 1.5" dia, complete with fittings. | m | 40 | 10 | 400
4.3 | Brine reject line – uPVC PN16, 1.5" dia, complete with fittings. | m | 30 | 10 | 300
4.4 | Stainless steel flexible connectors – SS316, various sizes for pumps and filters. | No. | 6 | 100 | 600
5 | Instrumentation & Control
5.1 | Pressure gauges – glycerin filled, SS316, ranges: 0–10 bar and 0–25 bar. | No. | 6 | 50 | 300
5.2 | Flow meters – rotameter type, acrylic tube, 0–5 m³/h and 0–1 m³/h ranges. | No. | 2 | 200 | 400
5.3 | TDS/conductivity meter – inline type, digital display, 0–10,000 ppm range. | No. | 1 | 600 | 600
5.4 | Control panel – IP55, powder-coated steel enclosure, PLC-based, with HMI touchscreen, alarms, auto-shutdown for faults. | No. | 1 | 2000 | 2000
6 | Testing, Training & Commissioning
6.1 | Factory testing & pre-commissioning of RO system (FAT). | lump sum | 1 | 2000 | 2000
6.2 | On-site installation, testing, and commissioning (including all tools & consumables). | lump sum | 1 | 3000 | 1800
6.3 | Operator training – minimum 2 days, covering O&M, troubleshooting, and safety. | lump sum | 1 | 800 | 800
| Total |  |  |  | 95750

## 50 M3 WDP
BOQs for Brackish Water RO Plant (50 m³/day) in Salabouna - Port Sudan
Item No. | Description with Notes | Unit | Qty | Unit Rate | Total
|  |  |  | Select Currency | Select Currency
1 | Civil Works
1.1 | Site clearance, levelling, and compaction (remove vegetation, debris, and level to ±10 mm). | m2 | 100 |  | 0 | SDG
1.2 | Reinforced concrete foundations (400*400*500 mm) , C25/30 concrete, with T12@10 both way one layer steel bar ), for RO unit Container room. | m3 | 0.7 |  | 0 | USD
1.3 | Perimeter fencing (chain-link mesh 2.5 m height, galvanized, with concrete posts every 2.5 m, foundation 300 mm wide × 500 mm deep, 2 meters entrace gate with functional lock). | m | 20 |  | 0
1.4 | Guard room (3 × 3 x 2.5 m) – concrete brick walls, plastered inside/outside, steel door (70*200 CM), 1 window (100*120 CM), Isolated steel sheet roof (from water and heat Grade: >R5), supply and fix one fan and 12,000 Btu A/C (inverter), LED lighting and two 16 A sockets | lump sum | 1 |  | 0
1.5 | Separate room for solar system and batteries (4 × 3 x 2.5 m), concrete brick walls, plastered inside/outside, steel door (70*200 CM), Isolated steel sheet roof (from water and heat Grade >R5), supply and fix one fan and 12,000 Btu A/C (inverter), AFO fire balls, smoke detector and fire extinguisher (powder). | lump sum | 1 |  | 0
1.6 | RO plant room (12 × 2.4 x 2.4 m) Container with adequate ventilation fans, waterproof coating, and service trench, painted with WV visibilty outside | lump sum | 1 |  | 0
1.7 | Water Tank Base (3 x 3 x 1 m) - concrete bricks walls filled with compacted soil covered by 5 cm plain concrete C15 (indlude plastering works for walls, and non slip coating for concrete layer) | lump sum | 2 |  | 0
1.8 | 2 x 1 m Steel Sign board with WV Visibiltiy and project details | lump sum | 1 |  | 0
1.9 | Drilling raw water well intake (depth to be select in site, install 4" UPVC casing and screen, gravel pack and sanitary seal) complies with AWWA A100-97 | lump sum | 1 |  | 0
1.1 | Drilling raw water well intake (depth to be select in site, install 4" UPVC casing and screen, gravel pack and sanitary seal) complies with AWWA A100-97 | lump sum | 1 |  | 0
2 | Mechanical & Process Equipment
2.1 | Raw Water Feed Pump – Vertical Multistage SS 316 Pump – Capacity 5–6 m³/h @ 6–8 bar, motor 3-phase, IP55, TEFC; includes suction strainer, flexible coupling, non return and isolation valves. Complies with ISO 5199 / API 610 for pump design. Includes installation, alignment, and testing of water depth to aviod cavitation | No. | 1 |  | 0
2.2 | High-Pressure Pump for RO – Horizontal multistage SS 316, capacity 2.0–2.5 m³/h @ 16–18 bar; motor 3-phase IP55, TEFC, cartridge mechanical seal, with stainless baseplate and flexible coupling guard. Complies with API 610. | No. | 1 |  | 0
2.3 | Multimedia Filtration Unit – FRP pressure vessel, dia. 600 mm, height 1800 mm, max. pressure 10 bar; media: graded silica quartz + anthracite one meter height; manual multiport valve, sch.80 PVC piping; complies with AWWA B100. Includes media filling, testing, and flushing with 12 M^3/h for backwash | No. | 1 |  | 0
2.4 | Activated carbon filter – FRP vessel, 1 m dia × 1.8 m height, coconut shell carbon, iodine number > 1000 mg/g. NSF/ANSI 61 certified. Includes full carbon fill, backwash, and commissioning. | No. | 1 |  | 0
2.5 | Cartridge Filter Housing – SS 316, 5-round, 5-micron PP cartridges, rated 10 bar, quick-clamp closure, drain & vent ports; ASME BPVC compliant. Includes initial set of cartridges. | No. | 1 |  | 0
2.6 | RO membrane housing – FRP, 4" × 40" size, suitable for brackish water, 8 elements in series. | No. | 2 |  | 0
2.7 | RO membranes – Dow FilmTec BW30-4040 (or equivalent), salt rejection ≥ 99%, with perfurmance certificate from autherised seller | No. | 8 |  | 0
2.8 | Automatic Chlorination dosing pump – diaphragm type, 0–5 L/h @ 5 bar, PVDF head, with 50 L chemical tank. | set | 1 |  | 0
2.9 | Antiscalant dosing pump – diaphragm type, 0–5 L/h @ 5 bar, PVDF head, with 50 L chemical tank. | set | 1 |  | 0
2.1 | Chemical consumption for one month (NaOCl, CaCO3, Antiscalant) | set | 1 |  | 0
3 | Electrical & Solar Power System
3.1 | Solar photovoltaic panels – monocrystalline, 580 Wp, Tier 1, IEC 61215/61730 certified. | No. | 20 |  | 0
3.2 | MPPT solar charge controller – 150 V, 100 A, programmable, with LCD display. | No. | 1 |  | 0
3.3 | Lithium-ion battery bank – 15 kWh total capacity, ≥ 6000 cycles @ 80% DoD, rack-mounted, compatible with hybrid inverter | set | 2 |  | 0
3.4 | Inverter – hybrid type, 4 kW continuous output, pure sine wave, with grid/backup generator input. | No. | 3 |  | 0
3.5 | Electrical wiring & accessories – XLPE copper cables, armored for outdoor runs, complete with conduit, cable trays, breakers, surge protection, lighing protection & earthing system | lump sum | 1 |  | 0
4 | Plumbing & Piping Works
4.1 | Raw water pipeline – HDPE, 2" dia, with unions, elbows, tees, and valves. | m | 15 |  | 0
4.2 | Permeate storage tank 10 m³, food-grade, UV-protected, top manhole, vent filter, drain valve, float valve & overflow valve. | No. | 1 |  | 0
4.3 | Raw water storage tank – 5 m³, food-grade, UV-protected, top manhole, vent filter, fixed in tank base | No. | 1 |  | 0
4.4 | Permeate line – HDPE PN10, 1" dia, complete with fittings. | m | 40 |  | 0
4.5 | Brine reject line – HDPE PN16, 1" dia, complete with fittings & connected to brine water well | m | 30 |  | 0
4.6 | Stainless steel flexible connectors – SS316, various sizes for pumps and filters. | No. | 6 |  | 0
5 | Instrumentation & Control
5.1 | Pressure gauges – glycerin filled, SS316, ranges: 0–10 bar and 0–25 bar, two for each stage | No. | 6 |  | 0
5.2 | Flow meters – rotameter type, acrylic tube, 0–5 m³/h and 0–1 m³/h ranges, (±5% accuracy) | No. | 2 |  | 0
5.3 | TDS/conductivity – inline type, digital display, 0–10,000 ppm range with Auto temperature compentation of reading | No. | 1 |  | 0
5.4 | Control panel – IP55, powder-coated steel enclosure, PLC-based, with HMI touchscreen, alarms, surge protection, auto-shutdown for faults & manual override mode. | No. | 1 |  | 0
6 | Testing, Training & Commissioning
6.1 | On-site installation, testing, and commissioning (including all tools & consumables). | lump sum | 1 |  | 0
6.2 | Operator training – minimum 3 days, covering O&M, troubleshooting, and safety. | lump sum | 1 |  | 0
6.3 | Maintenance/cleaning tools to individuals managing the plant (Screwdriver Set, Pliers, Wire Strippers, Adjustable Wrench, Allen Wrench Set, Socket Set, Flashlight, Safety Goggles, Gloves, Overall, Cleaning Supplies: Besom, Broom, Gloves, Brush, Mob, Squeegee, Wire Brush, Bucket (Other consumables) | lump sum | 1 |  | 0
6.4 | Clean in Place Chemicals for three clean cycles (Citric acid, NaOH) | lump sum | 1 |  | 0
| Total |  |  |  | 0
BOQs for Water Distribution Point in Bait Elshabab IDPs Site - Port Sudan
Item No. | Description with Notes | Unit | Qty | Unit Rate | Total
|  |  |  | Select Currency | Select Currency
1 | Civil Works
1.1 | Site clearance, levelling, and compaction (remove vegetation, debris, and level to ±10 mm). | m2 | 10 |  | 0
1.2 | Water Tank Base (3 x 3 x 1 m) - concrete bricks walls filled with compacted soil covered by 5 cm plain concrete C15 (indlude plastering works for walls, and non slip coating for concrete layer) | lump sum | 1 |  | 0
1.3 | Excavation (40 x 50 Cm) and backfilling after laying the pipes | LM | 500 |  | 0
1.4 | construction of water distribution point in front the storage tank (5 taps) | lump sum | 1 |  | 0
1.5 | Construction of soak-away pit | lump sum | 1 |  | 0
1.6 | Paint WV Visibiltiy and project details in Tank Base | lump sum | 1 |  | 0
2 | Plumbing & Piping Works
2.1 | Water storage tank – 10 m³, food-grade, UV-protected, top manhole & vent filter, drain valve, float valve & overflow valve. | No. | 1 |  | 0
2.2 | Water pipe line – HDPE PN10, 1" dia, complete with fittings and connected to storage tank | LM | 500 |  | 0
2.3 | Supply and install of 2 HP, 140 L/min, 45 Head | lump sum | 1 |  | 0
| Total |  |  |  | 0