## BoQ & Spec.
Project Name : Integrated food Security and Livelihood Support for Communities in Gedaref and Kassala State
Funded by: EU
Implemented by: ZOA International, Sudan Office
Location Gedaref State, Al-Mafaza Locality
Position: Heleba Hafir, Heleba village
Coordinates: N 13.680643⁰ E 34.833971⁰
Activity name: Drilling of water borehole near the Haffir
Activity Category: Water for Humans
Item. No | Description | Unit | Quantity | Unit Rate in (-----) | Total in (-----)
1 | Drilling of 6 inches Borehole in the fractures of basement rocks
1.1 | Site clearance by removing bushes and cutting & removing the surface soil for 30 cm depth with dimensions of 10*10 m, and discard the debris away, the measures for cutting to be taken from the lowest point at the construction plot | Job | 1 |  | 0
1.2 | Backfill the excavated area ( 7*7 meter ) with selected well graded soil and apply well compaction for it ,to the satisfaction of the site engineer using mechanical compaction to a height of 30 cm compacted soil layer above the original ground surface level measured from the higher level at the projected position and levelled perfectly | cubic meter | 15 |  | 0
1.3 | drill a borehole , Use drag bit diameter 12 inches to drill superficial deposit layer and bit with diameter 8 inches to drill the fracture. The well profile and drilling samples, tests' results are essential & crucial part of the job to be reported and submitted with the job completion | meter length | 55 |  | 0
1.4 | Provide and install P.V.C pipes conducter using pipes with specifications: ( 10 inches 10 bars 3 meter length for pipe) | meter length | 12 |  | 0
1.5 | Supply & Install P.V.C , 6 inches, 3 meters length, includes (4) filter to encasing the well. Please note:* well may not need encasing after drilling this determinate by well site geologist. In this case we return back cost value of the P.V.C. | meter length | 43 |  | 0
1.6 | provide and cast concrete protecting block (1W*1L*1d) meter ( 0.5 meter rising out of ground final level while 0.5 meter below ground level) surrounding the conductor using concrete mix (1:2:4) well compacted with vibrator and well cured and uniformed shaping, fix a cap cover for the well safely after the job completed using 5mm thickness steel plate one open and one blind flanges with gaskets & clamps and screwed to the conductor | Job | 1 |  | 0
1.7 | Cleaning by pumping till tubidilty is below 5 NTU then disinfect the water well . According to the State water corporation standards and acceptance. | job | 1 |  | 0
1.8 | Constant-rate Pumping test for productivity determination to be applied for continuous 24 hours minimum | Job | 1 |  | 0
1.9 | Conduct a physical , chemical and bacterial testing for water sample at an accredited laboratory by SWC & WES | job | 1 |  | 0
| Total in (----------) Please write the currency |  |  |  | 0
| Vat 17% |  |  |  | 0
| Grand Total in (----------) Please write the currency |  |  |  | 0