## Activity 17 - 50KW System
IMC - Sudan - Golo - Central Darfur
S. Olayan Foundation
BoQ for Solar Power Unit to Power Golo Hospital( 50 KW- System) - LOT 8
Note: All materials should be high quality, and rates include all necessary labour costs and tools, and all work done under IMC Engineer Supervision. The contractor should arrange for a site visit before submitting a bid.
| No | Activity 17 - Solarization of Golo Hospital | Unit | Quantity | Estimated Unit Price (SDG) | Estimated Total Price (SDG)
| 1 | Provision and setup of high-quality monocrystalline solar panels rated at 590 watts. The installation comes with all necessary accessories, including mounting screws (Mid clamp, End clamp) and MC4 connectors. Note that there are another 21 solar panels currently on site connected to two solar inverters, based on the engineer's directions. | عدد NO | 324 |  | 0
| 2 | Supply and installation of two (02) steel structures as mounting frames for solar panels, manufactured from galvanized steel with a thickness of 3 mm, designed to support a total of one hundred and sixty two (162) solar panels, each with a capacity of 590 watts, and engineered to withstand wind speeds of up to 120 km/h. The price includes all required accessories, complete assembly and installation works on the roof, and the construction of concrete foundations for each support, with dimensions of 50 × 50 × 50 cm, using a 1:3:6 concrete mix ratio, including proper curing by water spraying for three (03) days, tying, bolts, and nuts. The mounting structures shall be installed on Level ground using a total of fourteen (14) legs (supports), with a tilt angle of 17 degrees, oriented in a north–south direction- Further guidance to be provided by supervising engineer | عملية/ Job | 2 |  | 0
| 3 | Combiner Boxes and Fuses:Supply and Installation of Protection Panel Boards – divided as follows (including 2 panels, their internal components, installation, and all necessary accessories): 1. Fuses: 6 units, 20A (cylindrical/blade type) with holders, rated at 1000V DC, size 10×38 mm, replaceable. 2. DC Polarized MCBs: 3 units, 32A, 2-pole, for 1000V DC system. 3. Main DC MCCB for battery protection: 1 unit, 125A, non-polarized, for charge/discharge protection of batteries, including enclosure. 4. Main DC MCCB for battery protection: 1 unit, 150A, non-polarized, for charge/discharge protection of batteries, including enclosure. 5. AC Voltage & Current Regulators/Protectors: 2 units, 230V / 63A. 6. AC MCBs: 2 units, 32A, 2-pole, AC. 7. AC Changeover Switches: 2 units, 63A. Additional Notes: Glands will be used for proper connections between panels, batteries, and inverter. ( Project Engineer to determine with site inspection) | Units | 6 |  | 0
| 4 | Provision and setup of a 50 kW 48-volt Pure Sine Wave hybrid inverter, three-phase. Supporting a broad solar input range up to 500 volts per string. The cost covers all necessary installation accessories and is compatible with the specified lithium LiPoFe4 battery. | NO | 2 |  | 0
| 5 | Supply and installation of a 100-meter solar power cable, consisting of two copper conductors (positive and negative) in red and black colors, type PV-1F, with a cross-sectional area of 6 mm², made of fine-stranded wires. The cable shall be installed indoors inside Turkish PVC trunking sized 25 × 40 mm, and outdoors inside heavy-duty concrete conduits (Saudi or Omani origin) with a ½-inch diameter, including all required bends, fittings, and connections. The cable routing shall start directly from beneath the solar panels and continue until entry into the room, including fixing with clamps, and all accessories required for connection to the inverter. Two (2) strings shall be connected, each string provided with its own installation components. The price includes installation, fixing, and termination for all installation requirements. All string cables shall be routed inside flexible conduit (corrugated hose) in any locations where trunking or concrete conduits are not used, with clear identification markers for each individual string cable. The price includes all civil work related to the installation. | LM | 100 |  | 0
| 6 | Provision and setup of a 90 kWh LiFePO4 battery moduleLiFePo4 battery, Grade A, with a depth of discharge (DoD) of 90% and a lifespan of up to 6000 cycles. It operates at 51.2 volts and 300-320 AH, compatible and synchronouse with the inverter. The cost covers all connections and programming task, accept parallel connection. | NO | 2 |  | 0
| 7 | Provision of protection rack for the batteries set up and enclosure- made from local steel works | NO | 1 |  | 0
| 8 | Assorted cabling and lighting, Installation and connection accessories for the facilities | Item | 1 |  | 0
| 9 | Installation of earthing and surge protection and lightning arrester- pure copper and earth cable. | No | 1 |  | 0
| 10 | Installation, configuration, and electrical connection of an 80-100 watt wall-mounted fan for inverter cooling, including all accessories, from a Pakistani or Indian brand. | NO | 2 |  | 0
|  | Total Cost in SDG |  |  |  | 0